VENTREE

Industrial  Ventilation  System  Design  Templates

version  1.0

USER'S  GUIDE

SHAREWARE Software from:

WJD Computer Services

66 Raydon Rd. Ext.

York, ME  03909

(207)-363-2384

VENTREE  Industrial Ventilation System Design Templates

The VENTREE Industrial Ventilation System Design Templates

and this accompanying Users' Manual are being distributed as

SHAREWARE software.  SHAREWARE is an effort by software

developers to provide useful software at a lower cost to you than

commercial software.  SHAREWARE is not Public Domain software,

and it is not free.  The following explains your rights and

obligations as a user of SHAREWARE.

LIMITED LICENSE

Non-registered users may use this software for a reasonable

period of time (up to 30 days) to determine if it is suitable for

their purposes.  Use of this software after this trial period

requires registration.

Registration permits a user to use this software as

described in this manual on one single-user computer, unless

multiple copies have been registered in accordance with the

registration form.

Any user may copy this software for the trial use by

others subject to the above limitations and the following:

Only COMPLETE and UNALTERED copies of this software package

which include this manual may be distributed for trial purposes.

No fee or renumeration greater than actual cost of

providing the copy may be requested or accepted by the user.

COMPLETE and UNALTERED copies of this software package may

also be made available for trial use by others as follows:

Organizations which maintain a library of public domain

and user-supported software (e.g. computer users' groups) for

copying by their members may add this package to their library.

Operators of electronic bulletin boards may place a library

file of this software package in their download library.

Distributors of public domain and user-supported software

may include this software in their library provided that

diskettes are sold at nominal cost (not more than $10 each).

These templates may not be distributed with any commercial

products without written permission from the developer.

WARRANTY

This software and instruction manual are provided "as is"

with no warranty expressed or implied as to their performance,

merchantability, or fitness for any particular purpose.  The

entire risk as to the results and performance of this program is

assumed by you. The developer shall not be liable for indirect,

special, or consequential damages resulting from the use or

misuse of this software.

COPYRIGHT

This manual and accompanying VENTREE software are protected by

U.S. Copyright law (Title 17 U.S. Code).  Unauthorized

reproduction and/or distribution are prohibited.

Copyright (C) 1991 by William DeGrandpre, All Rights Reserved

i

VENTREE (SHAREWARE) Registration Form

Name: _____________________________ TITLE: ___________________

Company Name: ________________________________________________

Street Address: ______________________________________________

City: ________________________________________________________

State: _________________________  ZIP: _______________________

Country: _______________________  Phone: _____________________

Type of business: ____________________________________________

Number of computers or workstations: _________________________

VENTREE Source (associate, bbs, user lib, etc): ______________

The registration fee for 1-5 personal computers or local area

network (LAN) workstations is $20.00 per unit.  Fee schedules

for a larger number of units and site or corporate licenses are

available upon request.

Registration fee: ______________

Total enclosed: ______________

Please send check or Postal money order to:

WJD Computer Services

66 Raydon Rd. Ext.

York, ME  03909

Registration No: _______________________

ii

VENTREE  USER'S  GUIDE

Version 1.0

1.0  INTRODUCTION

1.1  Overview

The VENTREE Industrial Ventilation System Design

templates provide a powerful computational tool for the

calculation of isothermal local exhaust ventilation systems.

They combine the widely accepted velocity pressure method of

system calculation with data modeling concepts from computer

science and make them available in the flexible and familar

spreadsheet environment.  You can enter design data, compute it,

modify it, and recompute it as often as you like until you have

achieved an optimum design.  You can model existing systems

and test alternative modifications with your model.  You can

print or save the design at any time.

These templates are provided for Lotus 123 (TM of

the Lotus Development Corp), version 2.xx.  They will be ported

to other popular spreadsheets by the developer.

1.2  Background Knowledge

This manual describes the use of the VENTREE

Industrial Ventilation System Design Templates.  It is written

under the assumption that you are knowledgable in ventilation

system design techniques.  It also assumes that you are familar

with the basic operation of your computer, its DOS, and your

spreadsheet program.  As such, these topics are not discussed.

1.3  The Binary Tree Model

These templates are based upon a mathematical

structure known as a binary tree, one of the most extensively

studied nonlinear data structures.  As a mathematical model for

ventilation systems, it closely parallels the physical structure

of most local exhaust ventilation systems.  You do not have to be

a computer scientist, however to use these templates.  The tree

structure is incorporated into the templates, and needed

terminology is explained in this manual.  Figure 1 illustrates

the sizes and structure of the templates and provides a means of

relating your design sketch to the template model.  If you are

interested in the theoretical aspects of binary trees, you may

consult any text on computer data structures.

1.4  Disk Files

Version 1.0 of the VENTREE templates consists of the

following files:

VENTREE2.<ext> --- This is a "small" template which

provides the fastest calculation speed for small systems, i.e.

those not having more than one junction on the suction side of

the system.  It is a binary tree of depth 2.

VENTREE5.<ext> --- This is a "medium" template which

corresponds to a complete binary tree of depth 5.

1

VENTREE9.<ext> --- This is a "large" template which

contains the complete binary tree of depth 5 and a "pruned"

extension to depth 9.

SAMP2.<ext> --- This is a sample containing

ventilation system data (not balanced) in a VENTREE2 template.

VENTREE.DOC --- This is an ASCII (text) file of this

documentation.  It may be copied to the screen or a printer

using DOS commands.

READ.ME --- If present, this text file will contain

descriptions of any modifications to the templates not described

in this manual.

1.5  Disk Backup

Always keep backup copies of your master (blank)

templates and remember to back up your working copies.

1.6  Computational Accuracy

Each time a design data value is changed, all losses

affected by it are recomputed from the basic equations.

Approximating ratios are not used as repetitive approximations

can result in a cumulative error buildup.  This ensures that the

final results will be accurate.  These results may not agree with

those obtained by manual calculations, however, if approximating

methods were used in performing the manual calculations.

2.  ORIENTATION

2.1  Load a Template

Before attempting to design a new ventilation system

with these templates, you should become thoroughly familar with

their organization and operation.  After reading this manual,

load one of the templates (they are similar except for size) and

study the organization.

2.2  Columns

The first column contains row titles.  It is

locked (or windowed) so that it does not scroll off the

screen as you move across the sheet.  Each following column

represents one branch of a ventilation system.  A branch is

defined as a length of duct and its associated fittings from a

hood to a junction (a leaf node in tree terminology, or a

terminal branch of a ventilation system) or from one junction to

the next (internal node or branch). Branches are assumed to occur

in pairs, as shown on Figure 1, except for the singular ducts

which enter and exit the fan.  Two branches which enter a

junction at which they must be balanced always occupy adjacent

columns.  The fan suction duct corresponds to the root node of a

binary tree.  The discharge duct is treated as a special entity.

All duct, fitting, and hood data for a branch are entered in one

column.

2

2.3  Rows

The rows contain the individual design data elements

for each branch.  A detailed explanation of each row is contained

in Table I.  The first four rows are informational, providing

orientation within the template itself, the relationship to the

binary tree model, and a cell for user-entered branch names.

These rows are also locked to remain onscreen when you scroll

down the template.  The remaining rows contain design data or

computed values.  Static pressure loss data for balancing

junctions appears in the bottom rows of the template.  You will

notice that some row titles have asterisks (*) next to them.

Rows having one asterisk represent user entries for terminal

branches only (e.g. hood loss factors).  Rows having two

asterisks accept user-entered data for all branches (e.g. duct

length).  All other rows are computed (i.e. contain equations)

and should not be modified during data entry.

2.4  Default Modes

The templates have the following default modes of

operation.  Only the first is mandatory:

Columnwise recalculation.

Manually directed recalculation.

Titles locked to keep them from scrolling off the screen.

Cells containing formulas or text are protected.

2.5  Default Values

When a template is first loaded, it already contains

a complete set of data and computed values.  These data elements

are default values, frequently 0.  These values ensure that cells

or columns which are not included in your design do not introduce

errors into other cells or columns upstream.  The air flow rate

is a critical default value.  Every column has a default flow

rate of 0 CFM, and therefore no losses.  You define the structure

of your particular system by changing this default value in the

terminal branch columns (those containing hoods).  The template

computes airflow through internal branches automatically.

You enter data for your system by changing the default

values to those required by your design.  You must not change any

zero default values for which an entry is not required in your

design, or make entries in columns which do not exist in your

system.  Doing so may introduce errors.

2.5  Error Trapping

The equations in these templates contain some

measures to prevent erroneous data entries from affecting the

final results, however it is impossible to catch all possible

errors in a spreadsheet template.  Some of these measures are

discussed in this section.

A terminal branch is defined to exist by changing the

default 0 CFM airflow rate.  This default value prevents unused

columns from affecting any results.

Once a terminal branch is defined, all upstream branches of

the binary tree model which lead from the terminal branch to the

fan must exist, and their flow rates are automatically calculated

from those existing downstream.  This ensures that there are no

"disconnected" branches in the model.

3

Since the airflow in internal branches is computed, you can

only change flow rates in the terminal branches.  Although this

may seem inconvenient, this feature is essential to ensuring that

the final calculated losses are correct.

The method of computing losses within any branch depends

upon the terminal/internal status of the branch.  All branch loss

computations include fitting and frictional losses.  Hood losses

are only included in the final result for terminal branches.

Similarly, resultant velocity pressure corrections (VPR) are only

calculated for internal branches.  Only friction and fitting

losses are included in discharge duct calculations.

2.6  Try Examples

After you read this manual, you should try some

examples to become familar with how the templates work.  First

load SAMP2 and experiment with it.  Try to balance the system (it

contains only one junction, therefore its structure is obvious).

Change some of the design data values and observe the effects.

Next, select an example with which you are familar, determine its

tree configuration, and enter it into the appropriate template.

Balancing a familar system with the template is the easiest way

to become accustomed to its operation.

3.0  USING THE TEMPLATES

3.1  Design the System

These templates are computational tools.  They do not

dictate any particular design methodology.  As such, you will

follow the same procedures which you would use if you were doing

the calculations manually.  Using your knowledge of the processes

being controlled and field measurements, you should develop a

sketch showing the system configuration, including its hoods,

ducts, fittings, and air cleaning devices, along with the

required flow rate and velocity in each duct.  With this sketch,

and a reference which lists pressure losses as a fraction of the

velocity pressure, you are ready to begin calculating.

3.2  Overlay Your Sketch

Figure 1 shows the largest system which can be

calculated by each of the templates.  Each branch occupies one

column.  You can think of these as empty slots into which your

system design will fit.  Your first step, therefore, is to match

your sketch to one of the templates.  For the fastest calculation

speed, select the smallest template which fits your design.

Each branch in figure 1 is numbered.  These numbers

correspond to the "Binary tree branch no." row of the templates.

Notice the pattern which these numbers follow.  At any branch k,

the two branches downstream are numbered 2k and 2k+1.  The branch

upstream is the result of the integer division k/2.  The

discharge duct is treated uniquely, and is numbered 0.  The

easiest way to number a sketch is to work from the top down, i.e.

the discharge duct is 0, the fan suction duct is 1, the ducts

below the first junction are 2 and 3, and, in general, at any

junction the 2k, 2k+1 rule applies.  This numbering maps your

sketch into the template.  You select the appropriate template by

looking at the largest number which appears on your sketch.

4

3.3  Data Entry

Once you have selected and loaded the suitable

template, you are ready to enter your preliminary design data.

The recommended approach is as follows:

First enter the design volumes and minimum transport

velocities for all the terminal branches, and direct a

computation.  This will propagate the flow rates upstream and

complete recommended duct diameters for all the branches.

Note: after this calculation, some cells may indicate an

error condition.  This results from attempted division by zero

because the actual duct diameter is still zero.  This is of no

concern at this point in the calculation process.

Next, enter preliminary duct diameter selections and the

dimensional and fitting loss data.  A second calculation at this

point will compute losses throughout the system and indicate the

state of balance in the preliminary design.  You can now proceed

to balance the system.

3.4  Balancing the System

Balancing the static pressure losses is done by

branch pairs at each junction, exactly as it would be done

manually.  You can change design values and observe their effects

by directing a recalculation of the sheet.  The only restriction

on data entry is that you can only modify airflow at terminal

branches.

3.5  Printing or Saving A Design

You can print or save your design to disk at any time

using your spreadsheet print and save functions.  Saving your

design is particularly important, and should be done regularly

during any work session.  If you have numerous designs on disk,

keep an index so that you do not accidently erase or overwrite a

needed file.

4.0  ADDITIONAL TECHNIQUES

4.1  Modeling Existing Systems

You can model an existing ventilation system with

these templates by entering physical measurements obtained from

the system.  The resulting computations will be within the

accuracy of the measurements and the loss factors chosen for each

component.  This type of model can be used to predict the effects

of proposed changes to the system, e.g. reducing a duct diameter

to increase transport velocity or modifying a hood configuration.

4.2  Triple Junctions

These templates expect a binary configuration, but

your design may require three ducts entering one junction

(note that this is not a recommended design practice).  This

structure can be calculated by considering it as two binary

junctions joined by one duct having zero length and zero

fitting or friction losses.  Such an imaginary or virtual duct

can be computed by selecting the theoretical duct diameter (to

preserve velocity pressure) and entering 0 length and 0 fitting

losses (except possibly for a branch entry factor).

5

4.3  Large Systems

At some time you may encounter a system  which is too

large for these templates.  This situation can be handled as

follows:

Map as much of the design as you can into the largest

template.  Now visualize the portion of the system remaining

(assuming it only "overflows" at one branch) as a separate

system, map it into a template, and calculate it back through the

junction just below the duct which fit into the largest template.

To obtain a final loss value for this subsystem, you can make it

enter an imaginary fan through a duct with no losses (use a

virtual duct as described in 4.2 above).  Save the final static

pressure loss for the subsystem, then proceed to enter the main

part of the system.  The duct which joins the subsystem will

appear as a terminal branch in this main template.  After you

have determined the velocity pressure through this branch,

convert the static pressure loss in the subsystem to a fraction

of the upstream velocity pressure and enter it as a hood loss.

From this time on, any changes in the volume flowing through this

duct, and thus the subsystem, will be reflected through this

velocity pressure factor.  All losses are not linearly

proportional to the velocity pressure, therefore it will lose

accuracy if the volume through the subsystem is changed

substantially.  If you do make significant changes, you should

recompute the subsystem and then the main system to obtain a

final design.

5.0  CUSTOMIZATION

Spreadsheet templates are a unique form of software

in that the user has both the source code and the means to alter

it, and in that the code and data are contained within the same

file.  VENTREE users are authorized to customize their templates

for their own use, however, they are solely responsible for

the correctness and effects of any modifications which they make,

and they may not distribute these modified templates outside of

the site for which their copies are registered.  Examples of such

modifications include, but are not limited to, alteration of

display formats (usually a harmless modification), importing the

templates into another vendor's spreadsheet (most spreadsheets

will import Lotus 123 templates, however some control/format

information, including formula protection, may be lost in the

process), and programming the templates for additional output.

6

6.0  ERRATA

6.1  Professional Use

The license for this software sets strict conditions

for providing copies to prospective users in order to ensure

that they receive complete, original templates and a copy of

this manual.  It does not, however, impose any restrictions which

would prevent registered users from using this software in the

same manner in which they would use any other licensed software

package.

6.2  Technical Errors

Programming errors, or 'bugs' which cause incorrect

results should be reported to the developer immediately for

corrective action.  Do not report desirable enhancements or an

inability to perform calculations not within the intended scope

of this software as described in this manual as 'bugs'.

6.3  Comments and Suggestions

Comments on this software and suggestions for

enhancement or extended capabilities of future versions are

welcome from all users.  Any suggestions containing equations

must reference their source to be considered.  All suggestions

for future versions, whether submitted as a letter or as a user

modification to a VENTREE data file become the property of the

developer and may be incorporated in future versions without

compensation to the suggestor.

VENTREE is SHAREWARE software from:

WJD Computer Services

66 Raydon Rd. Ext.

York, ME  03909

Email (Internet):  wjd@cup.portal.com

7

Table I:  Row Usage in the VENTREE Templates

Note: Each paragraph lists the row number, the row title, and the

expected data entry or computed value in that row.

1.  VENTREE?   <VER 1.0> :

Row 1 is a title row, containing the template number,

version, and copyright notice.

2.  -- Parameters -- (Units) -- :

This is a heading line for the remaining row titles.

3.  Bnry Tree Branch Number :

The number in row 3 of each column is the binary tree

branch number.  These numbers reflect the relationship between

columns and system branches, as shown in figure 1 and are useful

in mapping a sketch into the template.

4.  Column down/adjacent/up :

This row provides orientation within the template itself.

It indicates, for any given column, which columns are located

down from, adjacent to, and up from that column in the binary

tree model.  The "down" entry will contain either "tr", which

indicates that the branch must be a terminal, or the first

column letter of the branch pair below it.  The "adjacent" entry

will be the column containing the adjacent branch which enters a

common junction, or a "-" if none exists.  The "up" entry is the

column which contains the branch upstream of the current branch.

5.  Branch ID (text) ** :

The cells in this row may be used to enter a text name of

each branch, if desired.

6.  ----- Flow Data ----- :

This is a column subheading for the next group of rows in

which basic flow data, e.g. CFM, is to be entered.  This row is

also used by the system to determine the actual status of

branches which may be either internal or terminal, depending upon

the particular system being computed.  It contains the design

flow of the branch pair.  Once you begin changing design flow

rates, this column will 'lag' other computations by one

calculation.  Since this row is used only for status, not

computation, this is of no consequence unless you accidentally

define a branch pair which does not exist in your system.  In

this case, change the design flow in both ducts back to 0 and

recalculate the template twice to clear this status indicator.

7.  Design Volume (CFM) * :

The design flowrate in cubic feet per minute (CFM) at

standard atmospheric conditions is entered in this row.  As

indicated by the single asterisk, it is a valid entry only for

terminal ducts, i.e. those which have hoods.  An entry in this

cell of a column used for an internal duct is ignored.

Changing the design volume in a terminal branch is one

means of balancing the system.

8

8.  Density Factor (dimensionless) * :

If the air entering a terminal duct is at a density

substantially different from standard, a density factor may be

entered so that the system will be calculated to maintain the

desired total mass flow.  Since these templates are isothermal,

the same factor must be used at all entries.  It is divided

into the design flow to produce actual flow, and has a default

value of 1.

9.  Actual Volume (CFM) :

This is the first computed cell in each column, and is

used in all subsequent volume calculations.

For terminal ducts, it has the value of the design volume

divided by the density factor.

For internal ducts, it is computed as the sum of the

actual volumes in the two ducts downstream of that duct.

10.  Design Velocity (FPM) * :

This cell is used to enter the minimum transport velocity

required in the terminal ducts.  An entry in this cell is also

recognized in the discharge duct column.

11.  Transport Velocity (FPM) :

For terminal ducts, this is the design velocity.

For internal ducts, it is computed on the basis of the

combined airflow entering the duct.

A nonzero entry in cell 10 of the discharge duct column

will be entered in this cell of that column, otherwise a computed

value will be provided.  This feature allows the designer to

treat the discharge duct differently for specific conditions.

12.  ----- Duct Data -----

This is another column subheading indicating that the

subsequent rows relate to duct parameters.

13.  Transport Diameter (Inch) :

This is the theoretical duct diameter required to maintain

the minimum transport velocity.  It is provided as a guide to the

designer in selecting a duct diameter.

14.  Actual Diameter (Inch) ** :

This cell, which is a user entry for all columns, contains

the actual duct diameter, in inches, selected by the designer.

It may be modified during the design process to increase or

decrease the air velocity in the duct.

15.  Duct Area (Sq Ft) :

This value is computed from the actual diameter, and is

used in subsequent calculations.

16.  Actual Velocity (FPM) :

The air velocity is computed from the actual airflow and

duct area values of rows 9 and 15

17.  Velocity Pressure (In WG) :

This is the actual velocity pressure existing within the

duct, and is computed from the row 16 value.

9

18.  VPR (In WG) :

In internal ducts, this is the "resultant" velocity

pressure from the air entering the duct from the two downstream

ducts, and is computed for use in determining if any VPR

correction is required.

19.  Duct Length (Feet) ** :

The design duct length is obtained from the preliminary

design sketches and is a user entry for all ducts.  A length of

zero is acceptable.

20.  Roughness Factor (dimensionless) ** :

The default value of 1 may be changed to suit the

designer's knowledge about the frictional characteristics of the

duct being used.  It is a multiplicative factor.

21.  Friction Loss (In WG) :

The branch friction loss is computed from cells 19 and 20

within each column using the velocity pressure equation for

friction losses.

22.  ----- Fittings -----

This is a column subheading indicating that the subsequent

rows relate to fitting data.

23.  Number of Elbows (number) ** :

This is a count of the 90-degree elbows in each branch.

Fractional values, like 0.5 for a 45-degree elbow, are allowed.

24.  Elbow Factor (VPF) ** :

The elbow factor is the static pressure loss due to each

90 degree elbow expressed as a fraction of the velocity pressure.

This factor depends upon the bend radius.

25.  Elbow Loss (VPF) :

Total elbow loss as a fraction of the velocity pressure is

computed as the product of rows 23 and 24.

26.  Branch Factor (VPF) ** :

A branch entry loss factor should be entered for ducts

which enter a length of straight duct at an angle.  This factor

depends upon the angle of entry.

The template imposes no restrictions regarding which

branch of any pair is the "main" duct and which is the "branch"

that experiences an entry loss.  The user chooses appropriately.

27.  Other VP Losses (VPF) ** :

This cell may be used to enter the fractional values of

any other losses which are proportional to the velocity pressure.

28.  Fixed SP Losses (In WG) ** :

This cell may be used to enter any losses directly in

inches of water.  It is intended for devices for which the static

pressure loss is known and will remain reasonably constant.

10

29.  Fitting Losses (In WG) :

The total static pressure loss from the elbows, branch

entry, and other fittings is calculated in this cell and is

displayed as an aid to balancing the system.

30.  ----- Hood Data ----- :

This subheading indicates that the following rows apply to

hoods.  Consequently, entries are for terminal branches only.

31.  Entry Factor (VPF) * :

This entry loss factor, typically used for simple hoods,

will be multiplied by the duct velocity pressure to obtain the

actual loss at the hood entry.

32.  Acceleration (VPF) * :

This acceleration factor, like the entry factor, is

applied to the duct velocity pressure.  Its value is usually 1.

33.  Hood Loss (In WG) :

This is the total hood loss resulting from the duct

velocity pressure and the entries in rows 31 and 32.

34.  ----- Slot Data ----- :

This column subheading delimits the subsequent rows as

applicable to slot and plenum type hoods only.

Caution:  Velocity pressure factors in this section are

applied to the slot velocity pressure, not the duct pressure. The

designer may use any combination of hood (rows 31 and 32) and

slot factors as necessary to correctly compute any hood.

35.  Number of Slots (Nmbr) * :

This value must be positive for meaningful results.

36.  Slot Length (Inch) * :

The length of one slot in inches.

37.  Slot Width (Inch) * :

The width of one slot in inches.

38.  Slot Area (Sq Ft) :

This cell shows the total slot area in square feet

computed from the three above values.

39.  Slot Velocity (FPM) :

The velocity expected through the above slots is computed

from the standard V=Q/A.

40.  Slot VP (In WG) :

This is the slot velocity pressure which will be used in

subsequent slot loss calculations.

41.  Slot Factor (VPF-S) * :

This cell may be used for slot entry losses expressed as a

fraction of the slot velocity pressure.  Its default is 1.78.

11

42.  Acceleration (VPF-S) * :

This cell may be used for acceleration losses chargeable

to the slot velocity.

43.  Slot Loss (In WG) :

The static pressure loss due to the slots is displayed as

an aid to balancing the system.

44.  ----- Branch Data ----- :

It is below this subheading that branch and cumulative

loss data is displayed, along with balancing information.

45.  VPR Addition (In WG) :

A computed value will appear in this row for internal

ducts only if an additional static pressure compensation is

required.

46.  Branch SP (In WG) :

The total static pressure loss in the branch being

computed appears in this cell.  It is the sum of all the

individual losses from friction, fittings, hoods, etc.

47.  Cumulative SP (In WG) :

This is the total static pressure loss in the system back

to the junction being examined.  It is computed as the sum of the

branch static pressure loss and the maximum loss occurring in the

two downstream branches.

48.  Governing SP (In WG) :

At any junction, the largest loss between the two branches

entering the junction is considered the governing value.

49.  Ratio (Max/Min) :

The ratio of the governing static pressure to the lower

static pressure for any branch pair entering a junction is

displayed in the second column of any pair of ducts.

This value is displayed as a ratio rather than a percent

for computational usage.  A pair of branches is balanced within

10 percent if the ratio does not exceed 1.10.

50.  Revised Flow (CFM) :

The increase in flow necessary in the branch having the

lower static pressure loss is computed as a convenience to the

designer.  It is calculated from the SP ratio, and is accurate

for terminal branches.  For internal branches, this estimate may

be excessive.  An increase of approximately one-half of the

computed value is often adequate to balance the junction.

51.  Fan Data in Column ... :

This row title indicates where the fan data is displayed.

In the smallest template, it is located immediately below this

row.  In the larger templates, it is calculated in the column

immediately after the final tree branch column.  The following

fan data elements are displayed:

Total volume (CFM).

Fan total pressure (In WG).

Fan static pressure (In WG).

SP correction factor for negative fan inlet pressure.

Corrected volume (CFM).

Corrected fan SP (In WG).

12

VENTREE

ver 1.0

Industrial Ventilation System Design Templates

VENTREE2 has branches 0-3          ^            Ducts denoted by _ and |

| 0

VENTREE5 has branches 0-31         |            Junctions denoted by _|_

@ Fan

VENTREE9 has branches 0-511        |            Terminals denoted by ^

| 1

____________________|____________________

|                                       |

| 2                                     | 3

__________|__________                   __________|_________

|                   |                   |                  |

| 4                 | 5                 | 6                | 7

____|_____         _____|_____         _____|_____        _____|____

|        |         |         |         |         |        |        |

| 8      | 9       | 10      | 11      | 12      | 13     | 14     | 15

_|___   __|__     __|__     __|__     __|__     __|__    __|__   ___|_

|   |   |   |     |   |     |   |     |   |     |   |    |   |   |   |

|16 |17 |18 |19   |20 |21   |22 |23   |24 |25   |26 |27  |28 |29 |30 |31

|   |   |   |     |   |     |   |     |   |     |   |    |   |   |   |

L   |   ^   ^     ^   ^     ^   ^     ^   ^     ^   ^    ^   ^   |   R

_|____                                                    ____|_

|    |                                                    |    |

|34  |35                                                  |60  |61

|    |                                                    |    |

^    ^                                                    ^    ^

L                                 R

______|__________             __________|______

|               |             |               |

| 32            | 33          | 62            | 63

______|______      ___|___       ___|___      ______|_______

|           |      |     |       |     |      |            |

| 64        | 65   | 66  | 67    |124  |125   | 126        | 127

__|___     ___|___   |     |       |     |   ___|___      ___|__

|    |     |     |   ^     ^       ^     ^   |     |      |    |

|128 |129  |130  |131                        |252  |253   |254 |255

|    |     |     |                           |     |      |    |

|    ^     ^     ^                           ^     ^      ^    |

__|____                                                      ____|__

|     |                                                      |     |

|256  |257                                                   |510  |511

|     |                                                      |     |

^     ^                                                      ^     ^

Figure 1

13