#l---+--LT1----+-T--2----T----3--T-+----4T---+---T5----+-T--6----T----7--R-+----r

|

|

|

|

|

|

|

|

|

|          ELECTRC8

|          --------

|          Copyright 1991, by Robert J. La Capra

|          All Rights Reserved

|

|          Shareware Distribution Version

|

|

|

|

|

|

|

|

|

|          Robert J. La Capra

|          50 Hillside Terrace

|          Andover, NJ 07821

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

|

-- Table Of Contents --

Shareware ................................................ I

Disclaimer ............................................... II

Included Files ........................................... II

Introduction ............................................. 1

MENUS - Main And Function ................................ 2

DATA INPUT ............................................... 2

BOX FILL & SIZING CALCULATIONS

Device Box Fill Calculations ........................ 3

Junction, Pull Box Calculations:

Straight Pull .................................. 4

Angle or U Pull ................................ 4

CONDUIT SELECTOR ......................................... 5

COST TO OPERATE .......................................... 5

LIGHTING CALCULATIONS (Zonal Cavity Method) .............. 6

MOTOR CALCULATIONS

Branch Conductor Sizing ............................. 9

Fuse or Breaker Sizing .............................. 9

Overload Protection Sizing .......................... 9

PIPE & WIRE SELECTOR AND COSTCOMP ........................ 10

REFERENCE TABLES

Equipment Grounding Conductor ....................... 11

Grounding Electrode Conductor ....................... 11

Killowatt - Ampere Table ............................ 11

Underground Cover Requirements ...................... 11

Metal Device Box Table .............................. 11

Standard Pull & Junction Boxes ...................... 11

Standard Fuse & Breaker Table ....................... 11

Transformer Kva - Ampere Table ...................... 11

SETUP

Color Defaults ...................................... 11

VOLTAGE DROP CALCULATOR .................................. 12

Registration ............................................. 13

Registration form ........................................ 14

=  Shareware  =

Shareware is a term used to describe a software distribution or

marketing method. Under the shareware concept, software may be

freely copied and passed along to others, or distributed through

bulletin board systems, shareware distributors, etc...

As a recipient of a shareware program, you may use the software

for a short trial period to determine if it meets your needs. If

it does, you must pay the registration fee to the author of the

program. By paying the fee, you are granted the right to retain

the software for your own use. If the software is not suitable,

then you are not obligated to pay the fee, but you must not

continue to use the program.

The shareware system provides substantial benefits to you:

1. You get to try out the software before you buy it.

2. Shareware is much less expensive than comparable commercial

packages. You don't pay for marketing and packaging.

3. Many programs have been developed by expert programmers who

would never consider marketing their products commercially.

All they ask in return is a small fee to compensate them for

the considerable time and effort they have invested in the

development, testing and support of their products.

4. Shareware authors are much more responsive to the users'

requests for bug fixes, added features, special modifications,

etc...

The system is based entirely on the honor system, and usually

works well. Most people are honest and wouldn't violate the trust

placed in them by the author of the software.

Shareware is not free software. The author counts on your

integrity. If you intend to continue to use the program, please

register using the form at the end of this manual, or the form

included in the file "ELECTRC8.REG". Registration entitles you to

an expanded, 'Registered-User' version of this program. See the

end of this manual for details.

I

*  DISCLAIMER OF WARRANTY  *

|

| THIS SOFTWARE AND DOCUMENT ARE OFFERED "AS IS" AND WITHOUT

| WARRANTIES AS TO PERFORMANCE OF MERCHANTABILITY OR ANY OTHER

| WARRANTIES WHETHER EXPRESSED OR IMPLIED. BECAUSE OF THE VARIOUS

| HARDWARE AND SOFTWARE ENVIRONMENTS INTO WHICH THIS PROGRAM MAY

| BE PUT, NO WARRANTY OF FITNESS FOR A PARTICULAR PURPOSE IS

| OFFERED.

|

| GOOD DATA PROCESSING PROCEDURE DICTATES THAT ANY PROGRAM BE

| THOROUGHLY TESTED BEFORE RELYING ON IT. THE USER MUST ASSUME

| THE ENTIRE RISK OF USING THIS PROGRAM. THE AUTHOR OF THIS

| PROGRAM ASSUMES NO LIABILITY.

|

| DUE TO THE NATURE OF THIS PROGRAM, THE USER MUST BE FAMILIAR

| WITH THE SAFETY CONSIDERATIONS OF DESIGNING AND SAFELY

| INSTALLING ELECTRICAL WIRING SYSTEMS, IN ACCORDANCE WITH THE

| NATIONAL ELECTRICAL CODE. THIS PROGRAM IS NOT INTENDED TO

| REPLACE THE NEED FOR A QUALIFIED PERSON WHO IS EXPERIENCED IN

| THE ELECTRICAL DESIGN, CONSTRUCTION AND MAINTENANCE OF SAID

| ELECTRICAL SYSTEMS IN THEIR ENTIRETY.

|

|

|

|

|

|

| FILES INCLUDED ON ELECTRC8 DISK :

| -------------------------------------------------------

| Descrip.doc           Description of program

| Update.new            Changes in this version

| Electrc8.reg          Registration Form

| Electrc8.doc          This documentation file

| Electrc8.exe          Electrc8 program

| Electrc8.bug          Problem report form

|

|

|

|

|

| The importance of making a working copy of this or any other

| program disk cannot be too strongly stressed ! Please STOP NOW

| and copy all the files included on the ELECTRC8 disk to a

| blank formatted disk, and place the original in a secure place.

II

Introduction:

-------------

ELECTRC8 is designed to perform most common electrical contracting

and engineering calculations :

* Device, junction and pull box calcs.

* Conduit size selection for many combinations of different wire

sizes & types.

* Determine the cost to operate various loads at different

kwh charges.

* Lighting calculations based on zonal cavity method.

* Motor conductor, overcurrent and overload calculations.

* Calculate required wire and conduit size based on allowable

voltage drop.

* Quick reference tables for:

Grounding electrode conductor size

Equipment grounding conductor size

Underground cover requirements

KW to ampere tables

Transformer Kva to ampere tables

Metal device box size and capacity

Standard fuse & breaker ratings

Standard pull & junction box table

* Calculate voltage drop for various loads, voltages, wire size

and run lengths.

* All functions operate with 'what-if' capability. You can quickly

and easily change only the data you wish to, without having to

start a new calculation and re-enter all the required data.

Results are calculated and displayed as you make each change.

** All functions conform to the 1990 National Electrical Code.

The National Electrical Code is a copyrighted document of the

National Fire Protection Association, Batterymarch Park, Quincy,

MA. 02269.

Page 1

MAIN MENU:

---------

To run ELECTRC8, insert the program disk into the disk drive and

type ELECTRC8 then press ENTER or RETURN.

The program starts up with an opening screen with a prompt for you

to input a random number as displayed. Enter the number exactly as

it is displayed. The main menu will follow.

The main menu is a pull down type, structured as a horizontal bar

at the top of the screen with main titles displayed. Each of these

main titles represents a sub menu with one or more related program

functions.

To select specific program functions :

1. Press the hilighted letter of the menu item (main or sub).

OR,

2. Press the DOWN ARROW key to open the first sub menu, then use

LEFT or RIGHT ARROW keys to move between sub menus.

OR,

3. Position the hilighted block over a menu selection (main or

sub), then press ENTER.

DATA INPUT:

----------

All functions now have 'What-If' data entry routines. This method

of data input and calculation allows you to instantly see the

results of changing one data item at a time. You will not need to

restart the function from the beginning and re-enter all data just

to see the effect of changing one parameter.

The data input routines are similar in all functions. Use the UP

and DOWN ARROW keys, or ENTER, to move between input fields,

entering data as you go. Some fields limit your input to certain

values, and if you input data that is unacceptable, you will hear

a beep and will not be able to move from that field until the

correct data has been entered (or you leave the field empty).

Some functions require that you select one data item from a list.

This is done by pressing a function key which pops up a menu where

you will select one item from a list of choices. Use the UP or

DOWN ARROW keys to position the hilighted bar over your choice and

press ENTER.

After you have entered all required data, the calculation will be

performed and displayed. You can then change individual data items

and instantly see the results.

CAUTION:

When entering the last data item, or changing one data item which

was previously entered:

Be sure to record that change by moving from that field to another

field, or by pressing ENTER while still on that field.

Page 2

DEVICE BOX FILL CALCULATIONS:

----------------------------

Determines cubic inch volume required for boxes, as per NEC

section 370-6. Conductor size range is from #18 thru #6.

Free space (cubic in.) required for each conductor is as follows:

----------------------------------------

# 18 .. 1.5                  # 10 .. 2.5

# 16 .. 1.75                 #  8 .. 3

# 14 .. 2                    #  6 .. 5

# 12 .. 2.25

Deductions are as follows:

-------------------------

1 or more Fixture studs, cable clamps, hickeys  1 deduction

Each Strap containing 1 or more devices ....... 2 deductions

1 or more grounding conductors entering box ... 1 deduction

1 or more Isolated Ground conductors .......... 1 deduction

Enter the quantity of each size conductor within the box:

---------------------------------------------------------

A conductor running thru the box with no splices or connections

within the box should be counted as 1 conductor.

A conductor originating outside the box and terminating within the

box should be counted as 1 conductor.

Conductors, no part of which leaves the box (example ... a jumper

or pigtail from a splice within the box to a switch, outlet or

fixture mounted on the box), should not be counted.

** One or more grounding conductors, or, a second set of grounding

conductors (isolated ground ), should not be included in this

conductor count. They will be asked for later.

Answer the prompts for devices, clamps, fittings, ground

conductors, add'l ground conductors:

---------------------------------------------------------

Count each mounting yoke or strap containing one or more devices

as 1. Example... one duplex outlet - count as 1. two duplex

outlets - count as 2.

The remaining prompts are self explanatory. Answer Y for yes.

There is no need to answer N for any prompts which would be

answered as 'no'. A blank field is interpreted as 'no'.

A quick reference table of standard metal boxes and their cubic

inch capacity is available for viewing at any time, by pressing

F2. The current screen will be saved, and the table will be shown.

When you wish to return to the previous screen, press any key.

Page 3

JUNCTION, PULL BOX CALCULATIONS:

Straight Pull:

-------------

Calculates the minimum length, in inches, of pull and junction

boxes where raceways enter and leave the box at opposite ends. If

the wiring method is cable assemblies instead of raceways, first

determine the trade size conduit which would be appropriate for

the size and quantity of conductors in the cable assembly, then

use that conduit size.

If more than one raceway or cable enters and/or leaves either end

of the box, always use the largest size.

The method used to determine minimum box length for straight pull:

Eight times the trade diameter of the largest raceway.

The operation of this function is straightforward. Position the

hilighted bar over the largest raceway size for this calculation,

then press ENTER. The results will be displayed.

Angle or U Pull:

---------------

Calculates the minimum distance, in inches, between each raceway

entry inside a junction or pull box and the opposite wall of the

box, where raceways enter and leave the box at angles. If the

wiring method is cable assemblies, see the explanation above,

under 'Straight Pull'.

The method used to determine minimum distance for angle or U Pull:

Six times the trade diameter of the largest raceway, PLUS,

the sum of the diameters of all other raceway entries in any one

row on the same wall of the box. Use the row with the largest

total diameter of raceways.

A quick reference table of standard boxes and their cubic inch

capacity is available for viewing at any time, by pressing F2. The

current screen will be saved, and the table will be shown. When

you wish to return to the previous screen, press any key.

Page 4

CONDUIT SELECTOR:

-----------------

The Conduit Selector allows you to quickly and accurately

determine the conduit size required for 1 or more conductors.

Calculations are based on the Dimensions and Percent Area of

Conduit and Tubing from table 4, and from Conductor Dimensions as

per Table 5 of the NEC. Maximum allowable percent conduit fill is

53% for 1 conductor, 31% for 2 conductors and 40% for more than 2

conductors, as per table 4.

Use the UP, DOWN, TAB or SHIFT+TAB keys to move the cursor to the

desired wire size/type position, then enter the quantity of that

size/type conductor to include in the conduit. If you want to

include other size/types of conductors into the same conduit, then

repeat the above procedure. You can enter any combination of

conductors in the same conduit.

NOTE: Several fields will show an asterisk ( * ). This represents

the unavailability of those sizes/types of conductors. Do not

alter those fields.

Pressing F2 at any time will show the results of the calculation.

The program will list all the sizes and types of conductors you

chose for the calculation, their individual areas, the total area

extensions, the grand total area for all conductors, the minimum

trade size conduit required, the total area for the calculated

conduit, and the percent conduit fill for the calculation. If more

data is available than will fit on the screen, you will be able to

use the UP and DOWN ARROW keys to scroll through the data.

Pressing any key will return you to the conduit selector input

screen with all previous data intact.

GENERAL CALCULATIONS

Cost to Operate:

---------------

Calculates the cost to operate a certain load a number of hours

daily for some number of days at a certain KWH utility charge.

POWER OF LOAD is the number of WATTS the load draws.

DAILY USE is the number of HOURS the load is operated per day.

NUMBER OF DAYS is the number of days the load is operated.

PRICE / KWH is the utility charge per killowatt hour.

(Example..  10 cents/kwh, enter .10)

NOTE: A value of ten cents/Kwk initially appears in the

'Price/Kwh' field, as an example only. You should change

this value to reflect your own price/Kwh charge.

After entering the above information, the program calculates and

displays the cost to operate the load for the number of hours

daily for the number of days at the chosen utility charge.

Page 5

LIGHTING CALCULATION ( Zonal Cavity Method ):

--------------------------------------------

Calculates the quantity of lighting fixtures required to light any

room or area to any desired footcandle level.

The Illuminating Engineering Society (IES) has devised a flexible

and accurate method for calculating lighting requirements, called

the ZONAL CAVITY METHOD. This method assumes that any room or area

to be lighted is made up of three cavities, the CEILING CAVITY,

the ROOM CAVITY, and the FLOOR CAVITY.

The CEILING CAVITY extends from the ceiling surface down to the

lighting fixture mounting level. If the lighting fixtures are

recessed or surface mounted then the value of the Ceiling Cavity

will be zero. If they are suspended some distance below the

ceiling then the value of the Ceiling Cavity is the volume of

space between the ceiling surface and the fixture mounting level.

The ROOM CAVITY extends from the fixture mounting level down to

the work height level. The work height level is the distance above

the floor where the required quantity of footcandles is to be

maintained (usually desktop or work bench level).

The FLOOR CAVITY extends from the work height level down to the

floor. If the required footcandles is to be maintained all the way

to the floor, then the Floor Cavity value will be zero.

Every surface exibits a certain ability to reflect light. Light

colored surfaces reflect more light than dark surfaces, so more

light will need to be provided in a dark environment. The degree

of a surface's reflectivity is referred to as it's Percent

Reflection value. Percent Reflection can be accurately measured

with a reflectometer, or standard reflectance tables can be

referred to, such as the following:

TABLE FOR INTERIOR ILLUMINATION DESIGN

----------------------------------------

COLOR                % REFLECTION

----------------------------------------

Flat white               75 - 85

Ivory                    70 - 75

Buff                     60 - 70

Yellow                   55 - 65

Light tan                45 - 55

Light green              40 - 50

Gray                     30 - 50

Blue                     25 - 35

Red                      15 - 20

Dark brown               10 - 15

------------------------------------------

Page 6

The MAINTENANCE FACTOR is a value determined from the anticipated

maintenance of the fixtures and reflective surfaces in the room or

area. The intensity of illumination produced by a lighting

installation will depreciate after some time due to lamp aging,

and dust and dirt buildup. The MAINTENANCE FACTOR is designed to

adjust for this. Typical values are from .5 to .8. (.5 for a

poorly maintained environment, .8 for well maintained).

Each lighting equipment manufacturer publishes data for the

COEFFICIENT OF UTILIZATION (CU) for each fixture type and size in

it's line. The CU of a fixture is a measure of it's efficiency

under specific conditions of room cavity values and effective

reflectance values.

The formulas used in the ZONAL CAVITY METHOD :

CEILING CAVITY RATIO = (5 * Hc (L + W)) / (L * W)

ROOM CAVITY RATIO =  (5 * Hr (L + W)) / (L * W)

FLOOR CAVITY RATIO = (5 * Hf (L + W) / (L *  W)

WHERE:

Hc = distance from ceiling to fixture level (in feet).

Hr = distance from fixture level to work height (in feet).

Hf = distance from work height to floor (in feet).

L = length of room in feet.

W = width of room in feet.

ROOM LENGTH and ROOM WIDTH values must be entered in FEET.

Decimal points are accepted (Ex. 125, 50.5, etc...).

CEILING HEIGHT and FIXTURE HEIGHT must also be entered in FEET.

Decimal points are acceptable.

WORK HEIGHT must also be entered in FEET. Decimal points are

acceptable. If you want the WORK HEIGHT to be equal to the

floor, simply enter zero.

FOOTCANDLE LEVEL is a measure of the intensity of light falling

upon a specific surface.

Page 7

Values for Percent CEILING, WALL, and FLOOR Reflectances must be

entered as whole numbers (50, 80, etc...) Exact values can be

obtained by use of a reflectometer, or a standard table for

interior illumination design can be referred to, such as the table

for interior illumination design on the previous page.

The value entered for MAINTENANCE FACTOR must be less than or

equal to 1. The value of between .5 and .8 will be accurate for

nearly all calculations. A value of 1 will exclude the MAINTENANCE

FACTOR from the lighting calculation.

NOTE: A value of .8 initially appears in the 'Maintenance Factor'

field, as an example only. You can change this value to

reflect your own conditions.

To select fixture type, press F2. The menu will ask you to select

either 'built-in fixture type' or 'specify fixture type'.

Built-In:

---------

Fixture types stored internally include Recessed Incandescent,

Fluorescent, and High Intensity Discharge. COEFFICIENT of

UTILIZATION (CU) values which have been compiled by IES are stored

internally for these fixtures. The internally stored fixtures are

representitive of their types, as are the internally stored lamp

types. You will get accurate results using them, but if you wish

to use a type of fixture not available internally, you can choose

to specify your own type.

Specify:

--------

If you choose to specify your own fixture type, you will be

prompted for the number of lamps per fixture, the quantity of

lumens per lamp, and, the coefficient of utilization (CU) of the

fixture. You will need to have the fixture manufacturer's CU

specs. LUMEN specs are available from various sources. Lamp

manufacturers will have lamp catalogs which will list LUMEN values

for their line of lamps.

After all data has been entered, the number of fixtures required

will be calculated and displayed.

Page 8

MOTOR CALCULATIONS:

-------------------

Branch Conductor Sizing:

-----------------------

Calculates motor branch circuit conductor size. NEC Article 430-

Part B, and, 430-6.

Conductor ampacity is based on 125 percent of motor full load

amperage, as determined from table 430-148.

Conductor types supported include THW, THWN, THHN, XHHW Copper,

THHN, XHHW Aluminum.

Fuse or Breaker Sizing:

----------------------

Calculates rating or setting of motor branch circuit overcurrent

protective device (Nontime-delay fuse, Time delay fuse,

Instantaneous trip circuit breaker & Inverse time circuit

breaker). NEC Article 430-Part D, and, 430-52.

Rating or setting is based on Full load amperage (from table 430-

148) of motor, multiplied by appropriate percentage factor from

table 430-152 for the selected device type. Article 430-52(a).

If this results in a value other than a standard size or rating of

overcurrent protection device, the next higher standard rating is

selected. Article 430-52(a), Exception 1.

Overload Protection Sizing:

--------------------------

Calculates motor overload protective device rating. Article 430,

Part C.

Rating is based on motor full load amperage (from motor nameplate)

multiplied by:

125 % if nameplate marked service factor is not less than 1.15, or

125 % if nameplate marked temp. rise is not over 40 degrees C., or

115 % for all others.

Access Keys Used To Select Motor, Wire & Overcurrent Parameters:

-----------------------------------------------------------------

Press:    To Select:                 Press:    To Select:

--------------------                 --------------------

F4        Volts                      F6        Code Letter

F5        Horsepower                 F7        Wire Type

F8        Overcurrent Type

At the 'Percent Motor Power Factor' field, entering 100 will

assume 100% power factor and exclude the motor's Power Factor from

the calculation.

After all data has been entered, the calculation will be performed

and the results will be displayed.

Page 9

PIPE & WIRE SELECTOR:

---------------------

Calculates the conductor size required to carry a certain load for

some distance while not exceeding a specific voltage drop

percentage, and the trade size conduit required to contain those

conductors.

Conductor types supported include THW, THWN, THHN, XHHW Copper,

THHN, XHHW Aluminum.

Conductor ambient temperature derating is supported, according to

the ampacity correction factors at the bottom of NEC Table 310-16.

Conductor ampacity derating due to the number of current carrying

conductors in the raceway is supported as per NEC 310-Note 8(a).

Six circuit types are supported:

--------------------------------

1 Phase 2 Wire(Phase & neutral, or 2 Phase conductors)

1 Phase 3 Wire(2 Phase conductors & neutral)

1 Phase 3 Wire(Above circuit from a 4 wire wye system)

3 Phase 3 Wire(3 phase conductors)

3 Phase 4 Wire Wye(3 phase conductors & neutral)

3 Phase 4 Wire Wye circuit with the majority of load consisting of

electric discharge lighting, computers, or similar equipment.

In the third circuit type above, the neutral will carry

substantial current, and will be considered as a current carrying

conductor in the pipe size selection. NEC 310-Note 10(b).

In the last circuit type above, the neutral will carry harmonic

currents, and will be considered as a current carrying

conductor in the pipe size selection. NEC 310-Note 10(c).

Data Input:

-----------

The 'Maximum Percent Of Voltage Drop' field will only accept whole

numbers in the range of 0 to 9. This will be the maximum

percentage of the supply voltage which can be dropped by the

circuit conductors. If you enter 0 in this field, voltage drop

will not be considered in the selection of the wire size.

The 'Full Load Amperage Of Load' is the rated or maximum amperage.

The 'Source Voltage' is the supply voltage for the circuit.

The 'Length of Run In Feet' is one way length from supply to load.

Press F2 to select the circuit type.

Press F3 to select the wire type.

Press F4 to select ambient temperature of the circuit conductors.

After you have entered the data, the program will calculate and

display the required conductor and pipe size.

Page 10

EQUIPMENT GROUND CONDUCTOR TABLE:

--------------------------------

To determine the required size equipment ground conductor,

as per NEC Table 250-95.

GROUNDING ELECTRODE CONDUCTOR TABLE:

-----------------------------------

To determine the proper grounding electrode conductor size,

as per NEC Table 250-94.

KW TO AMPERE TABLES:

-------------------

To quickly convert single and three phase KW values to ampere

values and vice versa. Pressing PG UP & PG DN scrolls between the

single phase and three phase tables.

UNDERGROUND COVER TABLE:

-----------------------

To determine the minimum cover requirements of conduit,

underground cable, and other raceways, as per NEC Table 300-5.

METAL DEVICE BOX TABLE:

----------------------

Table of metal device boxes and their cubic inch capacities.

STANDARD PULL & JUNCTION BOXES:

------------------------------

Table of standard pull & junction boxes and their cubic inch

capacities.

STANDARD FUSE & BREAKER TABLE:

-----------------------------

Table of standard ratings of overcurrent devices.

TRANSFORMER KVA TO AMPERE TABLE:

-------------------------------

To quickly convert single and three phase transformer Kva values

to ampere values and vice versa. Pressing PG UP & PG DN scrolls

between the single phase and three phase tables.

SETUP:

Color Defaults:

--------------

As supplied, the program starts up in black and white. Select

'Setup' from the main menu. Then select either Color Display or

Mono Display. Your choice will be executed, and saved to a disk

file, which will automatically be used for future program use.

Page 11

VOLTAGE DROP CALCULATOR:

-----------------------

Calculates the voltage drop on existing or proposed single phase

resistive AC circuits (100% power factor). Copper and aluminum

conductors from #14 to 2000 Kcmil are supported. The registered

user version supports 3 phase circuits.

The 'Length Of Run' is the length in feet of one conductor from

the source of power to the load terminals.

The 'Source Voltage' is the voltage measured at the source of

power.

The 'Amperage Of Load' is the current required by the load. For

example, if the load is a resistance heater requiring 10 amps to

operate as designed, then the AMPERAGE would be entered as 10.

The WIRE SIZE is in the range of #18 Awg to 2000 Kcmil. Do not

include the # sign or the letters Awg or Kcmil. Enter the numeric

size of the wire (ex. 14, 1/0, 250, 750).

The COPPER or ALUMINUM prompt is self explanatory.

After entering the above values, the program will calculate and

display:

1. The VOLTAGE DROP of the circuit (the number of volts dropped).

2. The VOLTS AT LOAD (the voltage delivered to the load terminals)

3. The % DROP (the percentage of the source voltage dropped)

Page 12

================================================================

REGISTRATION

----------------------------------------------------------------

When you register your copy of ELECTRC8, an expanded 'Registered

User' version of the software will be shipped to you immediately.

That version will support these additional functions:

* Three phase motor calculations:

Branch conductor sizing,

Overcurrent protection sizing, and

Overload protection sizing.

* Horsepower ratings not available in this version.

* Motor types not available in this version.

* Motor starting methods not available in this version.

* Additional general calculations - Single & 3 Phase:

Amperes when motor HP, PF and EFF. is known,

Amperes when watts or VA and PF is known,

Watts or VA when voltage, current and PF is known,

Motor HP when voltage, current, efficiency and PF are known.

* Short circuit calculations:

Start at a utility transformer or service entrance and

perform fault current calculations at various points along

the distribution system using BUSSMANN's Point-To-Point

method. Single and three phase calcs. Wire size & length,

single or parallel conductors - cu/al, magnetic/non-magnetic

raceways.

* Support of 3 phase circuits in the Voltage Drop Calculations.

* Print routines for all functions:

Print output to an ASCII disk file or to a printer.

* Elimination of the program's opening screen.

Page 13

ELECTRC8, Copyright 1991, By Robert J. La Capra

==  REGISTRATION FORM  ==

SHIP TO:

Name: _______________________________________________________

Company: ____________________________________________________

Address: ____________________________________________________

City,State,Zip:______________________________________________

Fee Enclosed: $__________

Where did you obtain ELECTRC8 ?:

_____________________________________________________________

Suggestions & Comments, if you wish:

_____________________________________________________________

_____________________________________________________________

_____________________________________________________________

_____________________________________________________________

_____________________________________________________________

_____________________________________________________________

_____________________________________________________________

==================================================================

Registration fee for ELECTRC8 is $45.00 for each user.

Purchase orders without payment attached cannot be accepted.

Send this form and registration fee to:

Robert J. La Capra

50 Hillside Terrace

Andover, NJ 07821

Once again, thanks for using and supporting ELECTRC8. As always,

any questions, comments and suggestion are welcome.

==================================================================

Page 14