The manual for the small version of HYDRONET 4.0 follows this order form...

ORDER FORM

Name: __________________________________________  Title: __________________

Firm: ___________________________________________  Phone: _________________

Address: __________________________________________________________________

City, State, Zip: _________________________________________________________

Both 5 1/4" and 3 1/2" diskettes are included in all packages.

Quantity  Product                                   Price each    Total

____________________________________________________________________________

HYDRONET 4.0 (single purchase)             $695.00 US

Additional HYDRONET 4.0 packages (no limit) 495.00

Upgrades from HYDRONET 3.0 to 4.0           150.00

please list serial numbers_______________________

HYDROFLO 1.2                                195.00

H-CALC 1.1                                   95.00

Combo - All 3 above products (save $140)    845.00

Calif. residents add 7.25% sales tax =

If desired, add $15 Express (2nd Day) within the U.S. per item =

Outside the US, Canada and Mexico, add $30 airmail per item =

Total Enclosed =

PAYMENT METHOD:

Check  or  M.O.  enclosed _____      or    COD  delivery _____

VISA ______  or MC ______  #_____________________________   Exp. _____/_____

Exact name on card _________________________  Bank issuing card ____________

Cardholder  signature ________________________________________

Foreign orders MUST be pre-paid in US Dollars drawn on a US bank.  Larger

Corporate and Gov't P. O.s accepted.   Please call for exact postage on

larger orders.   Quantity discounts and site licenses available.

Mail or FAX to:  ENGINEERING SOFTWARE

P. O.  Box 8128

Truckee, California  96162

(916)  582 - 1525    FAX (916)  582 - 8579

ENGINEERING  SOFTWARE'S

HYDRONET - Small version

Hydraulic Network Analysis Design Tool

Version 4.0

FOR THE PC/MS-DOS OPERATING SYSTEM

Software and manual written by

Brian Haulman

for

ENGINEERING  SOFTWARE

P.O.Box 8128

Truckee, California 96162

(916) 582-1525

FAX (916) 582-8579

Copyright (c) 1992, Brian Haulman

INTRODUCTION

HYDRONET is a hydraulic network analysis tool based on the popular

Hardy-Cross method.  A hydraulic network is a closed pressurized

fluid distribution system made up of pipes, fittings, valves, pumps

and reservoirs.  Examples of networks are industrial fluid conveyance,

municipal water supply, fire protection sprinkler, petroleum transport

and recirculating HVAC systems.  In a network, many interconnected

conveyance lines deliver liquids to numerous destinations simultaneously.

The change in flow through any single pipe influences the flow in all

other regions of the network.  The engineer must know the operational

steady-state flows and pressures throughout the system so that pipe and

pump sizes and system strengths can be specified to meet cost and safety

criteria.  These steady-state flows and pressures can only be determined

through an iterative flow adjustment process.  The Hardy-Cross method

lends itself to this task and, with the help of computers, the analysis

of hydraulic networks becomes a straight forward process.  Once a system

is defined by describing the components in detail, various operational

strategies can be investigated.

The full featured version of HYDRONET provides the ability to model large

systems of up to three thousand nodes and three thousand pipes, valves,

fittings and pumps.  Saving of datafiles, report output to file or printer

and digitizer support is also available.  This small version is limited to

systems of 26 nodes, 22 pipes, 16 valves and fittings and 2 pumps.  With

this limitation it is able to retrieve all the sample HYDROFLO datafiles.

It will only allow you to create 10 loops and 5 branches.  By using the Hazen-

Williams and Darcy-Wiesbach equations to determine pipe head losses, any

type of incompressible fluid can be modeled in an analysis when the proper

fluid properties and pipe conditions are known.  HYDRONET also provides

plots of the 2-dimensional system plan view, 3-dimensional view of the

overall system, hydraulic grade lines and pump performance curves.  A

complete menu of fittings and valves are available for incorporation into

hydraulic systems.  Various control valves can be modeled and will

accurately simulate their physical operating characteristics.  If you have

a Summagraphics or compatible graphics tablet (digitizer), x-y coordinates

for nodes can easily be entered and 2D and 3D system graphics can rapidly be

created.

INSTALLATION

INSTALL is the installation program and must be run before using the small

version of HYDRONET.  You must have 700K of space available on your hard

disk to install HYDRONET.  After starting your computer (booting-up), place

the HYDRONET diskette in a floppy drive and type...

drive:INSTALL   where "drive" is the floppy drive holding the diskette.

You will be prompted for the source drive and destination path to install

HYDRONET in.  The system files will be uncompressed and installed.

NOTE:  HYDRONET uses overlay technology so execution speed will be enhanced

when you use disk cache software.  Ideally, you want to use caching software

that makes use of Extended or Expanded memory and does not use up any of your

conventional main memory.  DOS's SMARTDRV.SYS is a good disk cache program.

To start the small version of HYDRONET, place yourself in the directory

where it was installed and at the DOS prompt type SMHN.  You wil then

specify the type of display adapter you have.  HYDRONET will take a few

seconds to load.

START-UP

While loading, HYDRONET does a quick check of your graphics tablet

(digitizer) if available, and will warn you of any possible problems.  If

you get a warning, be sure the cursor is in proximity and that you have

properly used the DOS MODE command (see above) to setup your serial port.

The top line of the main HYDRONET screen displays the HYDRONET copyright

notice and version number on the left and the current data filename on the

right with the word "Balanced" if the system has been solved.  Below that is

a space for the current system's title (description) if entered.  The bottom

line of the screen has the computer time and date on the left and the right

has a space reserved for error messages when they occur during system

operation.  The various keystrokes available as responses for any HYDRONET

prompt are displayed on the line just above the bottom of the screen.

HYDRONET uses the following menu and keystroke syntax...

To select an option from a displayed menu:

- Use the space bar or cursor arrows to highlight the option and

press RETURN (Enter), or

- press the first character of the menu option name.

To exit from a menu or operation:

- Press escape (Esc key).

(Note:  pressing escape repeatedly eventually brings

you back to the main menu but won't allow you exit to

DOS.  To fully exit HYDRONET, you must press "Y" at QUIT.)

An on-line help facility is available by pressing the F1 (function) key

anywhere during program execution except in graphic modes.  To obtain help

for a specific menu option, simply highlight the option (using the space

bar) without selecting it and press the F1 key.

When entering characters or numbers in data fields, a toggle between insert

mode and overtype mode is available by pressing the insert (Ins) key.  After

a desired numeric value has been input in a field, press the space bar once

and any remaining characters to the right will be disregarded.

UNDERLYING  THEORIES

THE HARDY CROSS METHOD

The Hardy-Cross method is based on two principles...

1. The sum of the head losses around a single loop always equals zero

(conservation of energy).

2. The sum of flows into and out of a node always equals zero

(conservation of mass).

HYDRONET automatically makes an initial estimation of flows in the system

then adjusts the flows in each loop to meet both the above conditions.  The

flows then approach the steady-state flow levels with each successive

iteration.  You provide the flow tolerance level at which HYDRONET will

exit the flow adjustment process.

The Hardy-Cross method is one of the most stable solution methods in

solving for steady-state pressures and flows throughout complex hydraulic

networks.  Certain instabilities can occur when the loops in a system are

not of near equal length in terms of nodes and elements or when impossible

conditions are set and cannot be met.  In general, the parameters displayed

on the screen when balancing will indicate the stability of the current

design.  If you start inputing smaller sections of a design and balance

the system as you go, you should have no problems.

The original work on the Hardy-Cross method is published in "Hardy Cross,

Analysis of Flow in Networks of Conduits or Conductors", Univ Ill. Bull.

286, Nov. 1936.  Also locate the books "Developments in Water Science" by

David Stephenson,  "Analysis of Flow in Pipe Networks", by Roland W.

Jeppson, Ann Arbor Science,  or "Analysis of Water Distribution Systems"

by Walski for additional information.

NODES

Nodes are the discrete physical points at either the junction of two

elements (pipes, valves, fittings or pumps), at the end delivery point

of a fixed flow line (branch) or at the location of the inlet or exit

of a reservoir (an unknown source or discharge of fluid).  The data

required for complete description of a node are: an optional description,

elevation, demand, head (pressure), and x-y coordinates.

There are two types of nodes used by HYDRONET...

1.) "fixed flow" nodes where the flow (demand) is set and the

pressure head is to be determined,

2.) "fixed head" nodes where the pressure head is set and the

flow is to be determined.

You are not allowed to set both the demand and head at a node.

FIXED FLOW NODES

HYDRONET determines the needed pressure head at "fixed flow" nodes that

will provide the specified demand flow.  In practice, the head at these

nodes is lowered until the demand is met.  Nodes between elements

where the demand is left at zero and the pressure is to be found, are

also of the "fixed flow" type.  The demand will always be out of the

system at these nodes.  If you desire to supply fluid into a system

at a node, it must be modeled as a "fixed head" node and start or end

a pseudo-loop (see pseudo-loops above).

FIXED HEAD NODES

Nodes at an inlet or exit of a supply of unknown flow but known head

are termed "fixed head" nodes (type 2 above).  Nodes that exist between

elements that are not in a branch line can be either "fixed head" or

"fixed flow" type.  Examples of "fixed head" nodes are...

- discharge or supply point from a pressurized or open tank.

- discharge or supply point from a lake or reservoir.

- discharge or supply point from a hydrant, sprinkler head or force main.

LOOPS

Loops consist of an alternating node - element - node - element - node

sequence.  HYDRONET uses two types of loops, pseudo-loops and closed loops.

PSEUDO-LOOPS

If a network is to be modeled as having flows into (and therefore out

of) the system, there must be at least one pseudo-loop in the

model.  These loops allow HYDRONET to determine the flow in or out based

on the user specified pressure head.  Pseudo-loops start and end with

"fixed head" nodes.  The head difference between the starting and ending

"fixed head" nodes maintain a constant head loss or gain in the

calculation of total head losses around a loop.  A sequence of nodes and

elements connecting two pressure mains or reservoirs (tanks) would be a

pseudo-loop.  All "fixed head" nodes must be at the beginning or end of at

least one pseudo-loop.  For example, if there are three "fixed head" nodes

(points of unknown inflow or outflow) in a system, there would be at least

two pseudo-loops connecting these nodes.  It will not hinder the balancing

process to use three pseudo-loops to connect all three "fixed head" nodes

to each other and in some cases will actually speed the convergence to a

solution.

CLOSED LOOPS

Single closed loops start and end at the same node.  They

trace a complete path around a loop of elements and nodes, ending at the

node where the loop started.  There may be many single closed

loops in both open (external inflows/outflows) and closed (recirculating)

loop systems.  This single "closed loop" is different from what is

commonly termed a "closed loop system".

A network modeled by HYDRONET need not have flow into and out of the

system.  There are many recirculating systems that can be modeled where

the fluid is moved around a system by an internal pump.  These "closed

loop systems" may have many internal single closed loops but have no

inflows into or discharges from a system.  They may have a recharge

source to replenish lost fluid but this is not part of a steady-state

analysis.  A "closed loop system" therefore has no pseudo-loops because

there are no "fixed head" nodes.  All demands at "fixed flow" nodes will

be zero.  An example of a "closed loop system" is a chilled or heated

water system in HVAC (Heating/Ventilation/Air Conditioning) systems.

BRANCH  LINES

Branches are fixed flow lines that remove flow from a system.  During the

iterative head loss balancing procedure, all network loops (pseudo-loops

and closed loops) are balanced.  After that, HYDRONET uses the head at the

node that starts the branch to perform simple head loss calculations for

all elements out to the ending branch node.

All the nodes in branches are of the "fixed flow" type so they will each

have fixed demands (fixed at a zero or non-zero flow) and HYDRONET will

determine the branch node pressure heads.  The last node will have the

fixed flow out of the line entered as it's demand.

PIPES

Both the Hazen-Williams and Darcy-Wiesbach equations are available for

the determination of major friction losses in pipes.  The question of

which equation to use depends on fluid conditions.  When Darcy-Wiesbach

meets Hazen-Williams conditions (see below) either equation may be used.

Comparing the results of both equations on 60 degree F water systems can

confirm proper modeling.

The empirical Hazen-Williams equation is available for water systems under

turbulent flow conditions at 60 degrees F. (15.6 degrees C. or turbulent

conditions for fluids with kinematic viscosity around

1.2x10-5 ft2/s).  To use this equation, Hazen-Williams coefficients are

needed for all pipes.  These coefficients have been determined by empirical

methods.  See Cameron page 3-8.  Using the Hazen-Williams equation allows

a system model to converge to a steady-state solution quicker than using

the Darcy-Wiesbach equation.

The fundamentally based Darcy-Wiesbach equation can be used for fluids of

different viscosities.  The kinematic viscosity of the fluid must be known

as well as the piping materials specific roughness (sometimes called

absolute roughness).  Fittings and valves must have custom K values or be

modeled as equivalent lengths of pipe.  HYDRONET uses the Newton-Raphson

method to solve the Colebrook-White equation which then determines the

Moody friction factor, f.  There is no need to manually look-up

friction factor values from the Moody diagram.

FITTINGS

The head loss (conversion of flow energy into heat) due to a gradual

bend in a pipeline is primarily caused by a secondary double spiral flow

which is superimposed on the main flow.  In moving around the bend, the

larger centrifugal force acting on the faster moving center core fluid

forces it toward the outside of the bend.  This added head loss occurs

for as much as 50 to 100 pipe diameters down the next pipe and does not

occur at the bend itself.  These head losses may be minor in systems that

have large lengths of pipe but may be a large component of the losses in

intricate systems with many bends and valves.

HYDRONET has a large selection of fitting resistance (K) coefficients

available for use in WATER systems.  Minor friction losses through

fittings (which includes inlets and exits) in water systems are modeled

by multiplying the velocity head by the appropriate resistance coefficient,

K (see Cameron Pg. 3-110 to 3-116).  HYDRONET automatically uses the proper

friction coefficient upon menu selection of the type and diameter.  Custom

fitting and valve coefficients can also be easily input by the

user.  Reducers, enlargements, orifices and nozzles are also able to be

modeled by HYDRONET.

Friction loss data for fittings and valves in systems modeling fluids

other than water are not readily available and those that are available

vary widely.  The best approach is to assume turbulent flow conditions

and specify that HYDRONET use the equivalent length method for fitting and

valves head losses.  This method models fitting and valve friction in terms

of the friction of turbulent flow through lengths of standard schedule 40

steel pipe.  The calculation of equivalent pipe length is based on the "K"

coefficient for water flow through the fitting or valve, the diameter of

the valve and the friction factor for complete turbulent flow in steel pipe

for this diameter.  Details of these calculations are in Cameron Hydraulic

Databook (pages 3-110, 3-119 to 3-122) and in the section entitled "USING

THE EQUIVALENT LENGTH METHOD" in this manual.

VALVES

A large selection of valves are available for use in water system design.

As with fittings, custom K values can also be input for valves not listed.

Control valves without fixed K values (ie, pressure and flow control

valves) can be used directly for non-water systems because their head

losses are set as needed and are not dependent on fluid conditions.  These

control valves slow down the balancing procedure substantially when used.

CHECK VALVES (CV)

Check valves allow flow in only one direction.  It is important to check

the operating flow velocity to ensure the complete opening of check valves

and therefore the correct friction factor.

PRESSURE REDUCING VALVES (PRV)

PRV's will not let the specified pressure be exceeded downstream.  If the

pressure is already below the specified level, the PRV will have no effect.

PRESSURE SUSTAINING VALVES (PSV)

The specified pressure will be maintained upstream if possible, with nearly

a complete shutoff if the pressure cannot be met.  Head losses are introduced

until the upstream pressure is above the specified level if possible.

FLOW CONTROL VALVES (FCV)

FCV's are modeled like PRV's by introducing enough head loss to decrease the

flow to the specified level.  If the flow is below the specified level, then

the FCV has no effect.

FIXED HEAD LOSS DEVICE (FHL)

The specified head loss will be introduced no matter what the flow is in the

line.  If convergence problems result in a system with a FHL device, try

removing it.  If the system then converges, try lowering the amount of head

loss.  The loop must provide enough added head (by pump or static head

difference in a pseudo-loop) to overcome the fixed head loss.

PUMPS & FLOW VS. HEAD DEVICES (FVH)

If you specify a pump from the element menu, you can select either a

pump or flow vs. head (FVH) device.  HYDRONET allows pumps to be modeled

by adding their head additions to loop head calculations.  FVHs are modeled

by incorporating their their head losses.  Pump curves are described by four

equidistant points and are fit to a cubic equation.  FVHs are described by

three equidistant points on a curve and are fit to a polynomial equation.  A

continuous function for head versus flow is then available for both

devices.  Pump manufacturers provide plots of their pump performance curves

and the four points can be easily taken from them.  The third point input

for a pump curve should be close to it's optimal operating point (second

point for a FVH).  Pump and FVH operation results for balanced HYDRONET

systems include flow rates and operating heads.

The REPORT - DETAIL PUMPS option lists a pump's suction head if the system is

balanced.  These values are critical in the operation of a pump to prevent

cavitation.  The Net Positive Suction Head (NPSH) must always have a positive

value.  The Net Positive Suction Head Available (NPSHA) depends on the system

design and, for an existing centrifugal pump, it is the total suction head in

feet (or meters) of liquid (absolute at the pump centerline or impeller eye)

less the absolute vapor pressure in feet (or meters) of the liquid being

pumped.  A pump's Net Positive Suction Head Required (NPSHR) can be obtained

from the pump's manufacturer.  The NPSHA should be above the pump NPSHR.  If

it is not, the situation must be remedied by using larger diameter suction

pipes by placing the pump closer to higher pressure sources (reducing

dynamic suction lift) or by placing the pump at a lower elevation (reducing

the static suction lift).

The suction head value presented by HYDRONET for a pump must have the

atmospheric pressure (when dealing with gage pressures) along with the

velocity head added to it minus the fluid's vapor pressure to approximate

the NPSHA (Net Positive Suction Head Available).  See Cameron Hydraulic

Data page 1-10 to 1-17 for more information.  Vapor pressures of hot

liquids may be very critical to the calculation as can the velocity head

of low head pumps.

MENU OPTIONS

FILE

The FILE option allows the retrieval from and the saving to disk of

HYDRONET datafiles.  Engineering Software's HYDROFLO datafiles can also

be read (see below).  HYDRONET datafiles store system information in a

compact proprietary binary format.  HYDRONET data filenames are appended

with the extension of " .NET " automatically.  You need not type in the

extension and you cannot override it.  You should not name any report

files or any other files with a .NET extension.

The RETRIEVE sub-option displays screens of HYDRONET data filenames.  Use

the space bar or arrow keys to highlight the desired filename and then

press RETURN to select the desired datafile.  You will then be asked whether

you want to load the file.  Any current system data information and changes

will be erased from memory and the new file will be loaded when you answer

"YES".  You should save any current system data, if it might be needed

later, before retrieving any datafile.

You may also press function key F2 and key in a custom path and

filename.  When you first press F2, the current path will be shown ready

for a new filename.  This is handy for the retrieval of HYDROFLO datafiles

in the current directory (see below).  Press escape (Esc) and an entire

path can be entered with a filename.  Datafiles retrieved will be read by

HYDRONET and the main menu screen will return with the filename displayed

in the upper right corner.  The new data is now available for use and any

previous system data is gone.

HYDROFLO files are NOT displayed along with HYDRONET filenames.  Press F2

(input a custom path and filename) at the RETRIEVE option and enter the

exact path and filename (including the .FLO extension).  If the HYDROFLO

system specified that the pump curve is to be prescribed, you must enter a

pump curve for the system prior to balancing.  HYDROFLO systems will

consist of one pseudo-loop when brought into HYDRONET.  Once in HYDRONET,

datafiles cannot be output in the HYDROFLO datafile format.

If there are more than 55 datafiles in the current directory, more

datafiles can be displayed by pressing the Page-down (Pg-Dn) key.  Each

successive screen will display the next available 55 datafiles.  To go

back to the first screen of filenames, press the Page-Up (Pg-up) key.

You may also press the F3 key to delete the highlighted file from disk.

If you answer "YES" to the delete prompt, the file will be erased from

disk completely.  Pressing the F4 key when a filename is highlighted,

displays the file's title (short description) if entered from the

UTILITIES - TITLE menu option.

When SAVE is selected, the current path and filename will be displayed.

If the current hydraulic design has not been saved or retrieved previously

(a new system), you must specify a filename.  If the file has a name it

will be displayed.  Pressing the escape (Esc) key will present the current

path ready for you to enter a new filename.  Pressing the escape key again

allows both a new path and filename to be entered.  When saving a datafile,

if a file with the same name exists, the following message will be

displayed:

file exists!   Cancel  Replace

Press "R" (replace) to overwrite the data file or "C" (cancel) or the

escape (Esc) key to quit the overwrite and cancel the operation.  Once you

have saved a datafile, it will appear in the main list available for use

later.

SETUP

The SETUP option is used to set the default data file directory (where

*.NET datafiles reside), pipe head loss equation, flow tolerance, units

system, units for node and pump heads and flows, fluid properties, bell

on-off, automatic pipe length calculation, use of the equivalent length

method and default friction coefficients.  The bottom of the screen

displays the current hardware configuration for your system.

The up or down arrow keys are used to move between the various input fields

(RETURN acts like the down arrow).  Pressing the escape (Esc) key (or moving

off the end of the fields) will lead to the prompt:

Reset current system to new values?     NO     YES

If the new parameter values aren't correct or desired, press the escape

(Esc) key or " N " to return to the main menu.  If they are correct,

press RETURN and the system will use the new parameter values and the

next prompt will appear:

Update default parameter file?     NO     YES

This prompt will only appear if the previous prompt is answered with a

"Y" .  A  "Y" (yes) response to this question will update the HYDRONET

default parameter file that automatically sets initial values upon

start-up.  This is a time saver in establishing new designs and provides

custom setups in multi-user environments.  For example, if an engineer

will always be using the Darcy-Wiesbach equation to analyze oil conveyance

systems, HYDRONET can start with these parameters automatically.  On hard

disk systems, each person can have their own user directory and HYDRONET

will be configured with their desired parameters and view only their data

files while using a central directory for the HYDRONET system files.

SETUP - PARAMETER DESCRIPTIONS

The DATA FILE DIRECTORY is the path where HYDRONET will look for data files

(shown in the FILE - RETRIEVE option).  This DATA FILE DIRECTORY should be

set to the users own sub-directory.  A user may make numerous sub-directories

each for a specific project so that just those datafiles will be displayed

when using FILE - RETRIEVE.  The named directory must exist and HYDRONET

will verify that it exists.  If you press the space bar (erase all characters)

in the DATA FILE DIRECTORY field, the current directory you reside in will be

inserted.  If running HYDRONET from another directory, be sure the HYDRONET

system directory is listed in your path.  (Type path at DOS prompt. See your

DOS manual.)

Pressing RETURN (or down arrow) highlights the HEAD CALCULATION EQUATION

field.  You may choose either the Hazen-Williams or the Darcy-Wiesbach

equation to calculate pipe head losses by pressing the left or right arrow

keys and then pressing RETURN or the arrow down key to select it.  The

differences in these equations is described in the preceding

"UNDERLYING THEORIES - PIPES" section.

The UNIT SYSTEM field is now highlighted.  English or Metric units may be

chosen as above, by pressing arrow right or left then pressing RETURN or

arrow down to select.  HYDRONET does not allow an automatic conversion of

hydraulic systems to or from English and metric unit systems.  Conversions

can be partially made by selecting the desired unit system, then using the

routines available in the UTILITIES option.

The SYS (System) FLOW UNITS are the flow units that element (all but pump

flows) and node flows will be displayed in.  Metric units of liters/second

and cubic meters/second and English units of cfs, gpm, Imperial gpm and

MGD (million gals/day) are available.

The FLOW TOLERANCE is the flow level at which HYDRONET will exit the

iterative flow adjustment balancing process.  The iterative process can

always be exited by pressing escape or the F2 key.

MENU OPTIONS - SETUP

SYS (System) HEAD UNITS are selected like flow units before.  If using

units of psi (English) or Kpascals (Metric), be sure to set the needed

specific gravity.

The DEFAULT SPEC ROUGH (SPECIFIC ROUGHNESS) or DEFAULT H-W (HAZEN-WILLIAMS)

COEFFICIENT can be set so that you have only to press RETURN when performing

pipe data input.  This does not change any currently defined pipe friction

coefficients.  To change ALL EXISTING pipe roughnesses to a new value, use

the UTILITIES - FRICTION option.  To change a specific existing pipes

roughness coefficient, enter the DEFINE option and press F2 when positioned

at the pipe.

The SPECIFIC GRAVITY value is needed for the conversion of head units to psi

or Kpascals.

The KINEMATIC VISCOSITY is required when using the Darcy-Wiesbach equation.

(See Cameron page 3-4.)

BELL ON-OFF selects whether the beep will be sounded for errors and data

input.  Pressing arrow-right or arrow-left will toggle the choices.

The PUMP HEAD & FLOW UNITS are the units in which head and flow values will

be displayed for all pumps and FVH devices.

The AUTO PIPE LENGTHS parameter specifies whether you want pipe lengths to

be automatically recalculated when ANALYZE or BALANCE is chosen.  This will

only be done if node coordinates are defined (non-zero).  If you leave a

pipe's length at zero, it's length is automatically calculated even if

the AUTO PIPE LENGTHS field is "NO".  When a pipe's length is not zero and

you change an adjacent node's coordinates, the length would not be

recalculated unless this field is set to "YES".

The USE EQUIV LENGTH METHOD field tells HYDRONET whether to model fittings

and valves as equivalent lengths of standard steel pipe.  This is needed for

modeling systems that convey fluids other than water.  The K coefficients

from the fitting and valve menus are for water systems only.

The bottom of the SETUP screen displays your current hardware configuration.

Re-run the HNINSTAL program to change this configuration if not correct or

if you change any of your hardware devices.

DEFINE

Use the DEFINE main menu option to enter element and node data.  The

sub-menu of " LOOPS  BRANCHES " allows either loop (pseudo-loop and closed

loops) or branch information to be entered.  Select LOOPS by highlighting

the word and pressing RETURN or simply pressing the letter "L".

GRAPHICS TABLET ALIGNMENT AND USE

If you are using a graphics tablet, when you enter the DEFINE option and

either edit or enter node data, you will be asked to align the tablet

with the diagram of your system.  This procedure may be postponed by

pressing the escape (Esc) key and using the Tablet Align (F6) function

later.  To align the tablet, the drawing of your system should be placed on

the pad so that the x direction runs parallel to the bottom line boundary

of the pad (x values increasing to the right) and the y direction is

parallel the right and left sides of the pad (y values increasing toward

the top).  You will enter two diagonal random points (x1,y1 and x2,y2)

from your drawing (ie., diagonal so that x1 does not equal x2 and y1 does

not equal y2).  Enter the x and y coordinates of the first point from the

keyboard.  Place the cursor (stylus) cross-hairs at that point and press

any button.  You will then be prompted to input the second point's

coordinates and click the any cursor button on the second point.  If no

response comes from the graphics tablet, press escape and make sure that

the DOS MODE command has been used to correctly setup the proper serial

port (see the INSTALLATION and START-UP sections).  To re-align the tablet,

while in the DEFINE option, simply press the F6 key when not editing element

or node data.  Repeat the procedure when inputing data from drawings larger

than your graphics tablet.  Press the escape (Esc) key to exit from the

tablet alignment procedure.

When positioned at a node's x coordinate field the statement to place the

cross-hairs at the node is displayed.  The proper coordinates will be

automatically inserted into the field when any button on the tablet cursor

is pressed.  If you do not wish to take advantage of the 2D and 3D graphics,

simply leave all node coordinates at 0 (zero).  They will be displayed as

" N/A " for not available.

LOOPS

Upon entering the LOOP sub-option of DEFINE, you will be prompted for a

loop number if a new design is being entered.  The loop number offered for

use will be the lowest loop number not yet used.  Use this number or enter

any other number you desire.  If you have retrieved a datafile, the first

screen of the lowest numbered loop in the system will be displayed.  Loops

can be entered in any order.

You will enter data for nodes and elements in the same order that they

occur in the loops of your design (ie, node - element - node - element -

node, etc.).  It doesn't matter if you enter the element and node data in

clockwise or counter-clockwise order.  The default value in the element

or node number field will be the lowest number that has not been used

in the current design.  You can overtype this value with any number

desired.  Upon pressing RETURN, the node data fields appear.  Once the

first node's data is input, an element menu will appear and allow the

next element's type in the sequence to be specified.  Once the element

type is selected by highlighting it and pressing RETURN, the input field

for the element will appear.  To input the second and remaining loops,

press the F9 key.  Select "LOOP" by pressing Return or " L " and enter

the loop number.  If the loop exists, it will be displayed.  If the loop

has not yet been created, you will be asked whether you wish to create it.

The current loop or branch number out of the total number in the design

and the current screen (page) out of the total number of screens in the

current loop or branch will be displayed on the bottom of the screen.

BRANCH LINES

HYDRONET allows fixed flow discharge lines to be included in a network

design.  These lines are not part of the actual "network".  Simple head

loss calculations are performed to find the heads at branch nodes.

The flow direction in a branch is always away from the node that starts

the branch (the node connected to the network).  On the screen this flow

appears left to right.  The direction is described on the bottom of the

branch input screen.  Branch input ends at the last discharge point

in the line.  This last node will have the flow through the branch entered

in it's demand field.  Other nodes in a branch may have a demand value

entered also.  The first node in a branch is the only node that may occur

elsewhere in the system since branches are outlets and do not flow

into other parts of the system.  Nodes with "fixed heads" are not allowed

in branch lines because the flows are fixed.  You are not allowed to have

a branch off of another branch because this would actually be a network

problem in deciding the flows in each line.

These sections detail the types of nodes and elements that may be used...

NODES

Node data includes optional description, elevation, demand (flow), head

(pressure) and optional x-y coordinates.  There are two types of nodes.

Nodes with a "fixed head" and those with a "fixed flow".  Do not enter

the optional description if you wish to save memory.  It will use up

memory much faster than just the essential node and element data needed

for network analysis.

If you are inputing node data and have just entered a fitting, valve or

pump, the elevation and X-Y coordinates will default to the values used

for the node on the other side of the element.

A node with a fixed pressure and an unknown inflow or outflow is a termed

a "fixed head" node.  Examples are any supply or outlet fluid level

(reservoir, tank, etc.) or an unrestricted supply or drain of fluid at

a specific elevation and pressure.  For a fluid reservoir at a specific

surface height, the surface elevation would be input in the elevation field,

a " ? " (question mark) would be input in the demand field (specifying

that flow is to be solved for), and zero would be entered in the head field

(if at atmospheric pressure using gage pressures).  If describing a node

for a pressurized tank or a system with absolute pressures, enter the non-

zero pressure in the head field.  As an example, a supply point (hydrant)

would have it's inlet elevation entered, then a " ? " in the demand field

and the actual or desired supply pressure entered for head.

A node with a head to be determined, is a "fixed flow" node, even if the

flow (demand) at the node is zero (zero is a fixed value).  These nodes will

generally be the internal points in a design (ie, points between pipes,

pumps, valves etc).  The elevation would be the physical elevation of the

node and the demand would be input as zero or a negative amount signifying

flow out of the node.  The head field therefore requires a " ? " to be

entered so that HYDRONET will solve for the resulting pressure.

When a system is balanced, "fixed flow" nodes will have the node's

pressure head highlighted in screen reports.  "Fixed head" nodes will have

the node's demand flow highlighted.  In file and printer reports, "fixed

head" nodes will have "fh" listed on the same line.

With the X-coordinate field highlighted, the coordinates of a node can

be specified.  This is optional and if you do not wish to use the 2-D or

3-D view of your system, then simply press RETURN to leave coordinates

at 0,0 and bypass this data.  You should not specify coordinates of 0

(zero) for x or y, unless you wish the coordinates to remain undefined

and not be plotted.  An undefined coordinate will be displayed as

"N/A".  HYDRONET will not plot nodes that have

coordinates of zero when displaying 2-D and 3-D graphics.  To enter the

coordinates of a node using a graphics tablet (see USING GRAPHICS TABLETS

previously), simply place the stylus (tablet cursor) cross-hairs at the node

when a node's X-coordinate field is highlighted and press any button on

the tablet's cursor.  The coordinates will appear in the fields and you

can press any cursor button again to re-do the values or press the RETURN

or ENTER key twice to accept the values.

PIPES

The data entered for pipes include optional description, diameter, length

and friction factor.  A non-zero diameter is needed to set up the default

system diameter.  The friction factor that appears will be the default

coefficient specified in the SETUP menu option and can be edited or another

friction value can be input.

If setting node coordinates, either manually or with a tablet, you

can set pipe lengths to zero and HYDRONET will calculate the distance

between the nodes and set the pipe length accordingly.  The lengths will

be calculated once ANALYZE or BALANCE is selected.  Once the pipe lengths

have been calculated and are non-zero, they will not be re-calculated unless

the AUTO PIPE LENGTHS field in SETUP is set to "YES" or you have set the

diameter to zero again.  Setting the AUTO PIPE LENGTHS field to "YES" makes

the calculation of pipe lengths automatic when node coordinates are changed.

FITTINGS

The fitting and valve coefficients automatically used by HYDRONET when

selected from the menus are for water systems only!  You must specify the

use of the equivalent length method in the SETUP option to model fittings

and valves in non-water transport systems if you do not have custom "K"

values. See the section on "USING THE EQUIVALENT LENGTH METHOD" for more

information.

The fitting menu lists numerous types including inlet and exit openings.

Use the cursor arrow keys to highlight the desired fitting and press

RETURN to select it.  You will then be prompted for the fitting's

additional description (optional) and actual inside diameter and

HYDRONET will use the appropriate K value for the fitting in it's head

loss calculations when you are modeling a water transport system.  You

have the option of pressing F2 on the fitting menu to input custom K

values.  NOTE:  The diameters you enter for fittings and valves should

be the actual inside diameter.  These inside diameters are converted

to nominal schedule 40 steel diameters (Cameron pg 3-120) to obtain the

proper coefficient from the tables in Cameron (pages 3-111 to 3-116).

Enlargements and contractions (reducers) are also available.  You are

required to have pipes on both sides of these fittings.  You need

to enter the full angle of change between pipe diameters.  HYDRONET will

perform a calculation for head loss using the inside diameters of the

elements on each side of the fitting.  (See the formulas on page 3-117 and

3-118 of Cameron).  Sudden enlargements/contractions

(reducers) can be specified by entering an angle of 180 degrees.

Nozzle and orifices can be modeled by HYDRONET.  Calculations are performed

as on page 2-8 of Cameron.  You are required to have a pipe

on at least one side of the orifice.  You will enter a C value that describes

the shape of the opening along with the inside diameter.  When using the

equivalent length method, nozzles and orifices will not be converted to

a length of pipe because a "K" fitting value is not used for these fittings.

If the fitting was previously defined and is to be edited, press F2 when

positioned at the fitting and it's data will appear for alteration.  You can

press the escape (Esc) key twice and retain the fitting's data at any

time.  You must press RETURN or the arrow down key at the last data field to

have any new data

changes take effect.  Pressing the escape (Esc) key only once presents the

fitting menu again to select a different type.  You can select a new fitting,

press F3 to enter a custom fitting or press F4 to display and select from the

valve menu.  When you simply enter a new inside diameter for a fitting type

from the menu, HYDRONET will use the appropriate K value (see pages 3-111

to 3-115 of Cameron).

VALVES

The valve menu lists numerous

types (gate valves, butterfly valves, various control valves etc.).  Use

the cursor arrow keys to highlight the desired valve type and press RETURN

to select it.  You will then be prompted for optional description and the

valve's inside diameter.  HYDRONET will use the appropriate K value

for it's head loss calculations in water systems.  Custom K values can

be entered by pressing F2 at the valve menu.  Editing previously defined

valves follows the same procedure as editing fittings described at the

bottom of the previous page.

CONTROL VALVES

Use of control valves substantially slows down the balancing procedure.

This is because the system must be balanced completely first, then solved

for head levels and valves checked for proper operation.  The system is

then balanced, heads solved for and the valve checked again.  This is

repeated until the system operates correctly.  If you know that you are

going to be doing a lot of design changes, you may want to set the

balancing tolerance higher to allow a faster, though less accurate, solution

until the design is near it's final form.  Then lower the tolerance to the

desired level.

Using valves that impart a head loss to the system (ie, PRVs, PSVs and

FCVs) to obtain a desired effect, takes energy from a system.  Most of the

time it is more desirable to design a system that doesn't need to burn up

head.  Head that is not wasted results in use of smaller pumps and overall

lower costs for a system.  Smaller diameter pipes burn up more head and,

therefore, provide more back pressure on the system.

- CHECK VALVES (CHV)

Check valves allow flow only in a specified direction.  The direction is

specified the same way pump flow directions are.  Use the right or left

arrow keys to change the direction that the displayed arrow points and

then press RETURN (or down arrow) to select it.

For stable balancing, loops should not have opposing directional devices

within them.  For example, while tracing around a loop, a check valve

allows flow in the forward direction while a pump in the same line allows

flow in the reverse direction.  Due to the flow adjustment procedure in

HYDRONET, this will severely handicap convergence during the balancing of

the system.  HYDRONET will print a warning but still attempt to solve the

problem. If the two devices flow in the same direction around the loop,

there should be no problem and the system will balance faster.   Most often

the problem will show up as a large head check error.  Each directional

device should be alone in it's own loop if possible.

If problems arise with check valve modeling, note those check valves in which

the flow is zero and remove that part of the loop that has no flow.  This is,

in essence, a dead end line.  If a check valve is observed to allow flow in

the proper direction, try replacing it with a custom valve with the same

friction coefficient.  The system will balance faster and be more stable.  It

is also important to check the operating flow velocity to ensure the complete

opening of check valves, and therefore, the correct friction factor.

- PRESSURE REDUCING VALVES (PRV)

When modeling PRV's, HYDRONET will not let the specified pressure be

exceeded downstream.  PRVs are modeled by introducing enough head loss

to drive the pressure down to the desired level.  These valves can be

used effectively in branch lines where there are no "fixed head" nodes

to complicate operation.  The data input for PRVs is an optional description,

inside diameter, allowed direction and desired downstream pressure.  The

elevation of the nodes on each side of the PRV should be the same and no

"fixed head" node is allowed on the downstream side since the valve already

attempts to do that.

- PRESSURE SUSTAINING VALVES (PSV)

When a PSV is used, the specified pressure will be maintained if

possible, with a nearly complete shutoff if the pressure cannot be met.  Head

losses are introduced until the upstream pressure is above the specified

level.  This type of valve is sometimes called a back-pressure valve.

- FLOW CONTROL VALVES (FCV)

FCV's are modeled like PRV's by introducing enough head loss to decrease

the flow to the specified level.

- FIXED HEAD LOSS DEVICE (FHL)

The specified head loss for a FHL device will be introduced no matter what

the flow is in the line.  If convergence problems result in a system with

a fixed head loss device, remove it and if the system converges,

try lowering the amount of fixed loss.  The loop must provide enough added

head through pumps or static head to overcome the fixed loss.

PUMPS & FLOW VS. HEAD DEVICE (FVH)

The data needed for the modeling of pumps and FVHs in a hydraulic design

include the flow direction and curve description.  The device description

is optional.  The pump and FVH flow direction is set by pressing the right

or left arrow keys to change the arrow direction displayed in the input

field.  Be sure that the arrow points to the correct downstream node.  Flow

opposite this direction will not be allowed.

To describe the flow vs. head curves for these devices, you will input

three (FVH) or four (pump) equidistant points from the device's curve.

The flow increment sets the distance between each point.  Pump curves are

fit to a cubic equation and FVH curves are fit to a polynomial equation.

For pumps, the four points of head begin with the shutoff head (the head

at which no flow can be push through the pump).  The remaining three

points on the curve are the head values at one, two and three times the

flow increment.  The desired operating point for the pump should be close

to the third point input for the curve.  It is very important that the pump

curve described is always decreasing - that is, the curve declines toward

the x-axis.  If the pump head does not decrease with increased flow, the

design may be unstable and may not converge.  The curve between the pump

shutoff head and the first point will be modeled as a straight line.  This

prevents problems where the curve has a hump or peak in it and the

balancing routine oscillates.

A FVH device creates a head loss, not a gain.  The first point of flow

vs. head will be at zero head and zero flow.  The rest of the points can

vary in increasing head but must be at equal increments of flow.  The

desired operating point for the pump should be close to the

second (middle) point on the curve.  The DEFINE option will display "FVH"

for the element at the top of the screen.  Once a pump or FVH is defined,

you can position the pointer at the device and press F5 to obtain a graphical

plot of the curve.  Pump and FVH results for balanced HYDRONET systems

include operating flow rates and heads.

EDITING...

This is a list of the keystrokes available for use in editing and moving

through the loop and branch data within the DEFINE option.

Right and Left Arrow keys

(F2) Edit existing node or element data

(F3) Delete an element and node

(Ctrl-F3) Delete sequence (loop or branch)

(F4) Insert element and node

(F5) Plot pump (& FVH) curves (when positioned at pump or FVH)

(F6) Align tablet

(F6) Print pump or HGL screens when viewing

(F7) Go to previous sequence (loop or branch)

(F8) Go to next sequence (loop or branch)

(F9) Go to (create) specific loop/branch

(Ctrl-F9) Copy loop/branch

(F10) Go to element/node

(Pg-Up) Go to previous screen (page)

(Pg-Dn) Go to next screen (page)

(1..9) Enter a previously defined element/node number

Their use and descriptions follow...

Right and Left Arrow keys

Use these keys to move the position pointer to the previous or next node

or element in the sequence.

(F2)  Edit

Use the cursor arrow keys (right or left) to move the pointer to an

existing element or node and press the F2 key to edit it's data.  The

input screen will be displayed with the current data.  You are allowed to

edit or re-enter any element or node data by inserting or overtyping the

numeric or text characters.  Pressing RETURN or the arrow down key at the

last data field accepts all changes to the data.  Pressing the escape

(Esc) key while editing retains the data without any changes made.  The

RETURN (Enter) key or arrow down must be pressed at the last data field

for all data entries or changes to be accepted.

(F3)  Delete node and element

When positioned at an element or node, pressing the F3 key prompts

for deletion of an element/node pair.  If the element and node are not

the ones to be deleted, press the escape (Esc) key.  You confirm the request

by highlighting the word "Yes", then pressing RETURN or pressing the "Y" key,

and the element and node will be removed.  Pressing "N" or escape will

retain the element and node.  If the pair occurs elsewhere in the system,

you will be prompted "Delete this node and element elsewhere in the

system?".  If you answer "Y", all other occurrences of this element/node

pair in system will be deleted.  You must specifically press the "Y" key

to acknowledge this prompt.  A lot of work will have to be undone if you

are wrong.

(Ctrl-F3) Delete loop or branch

Pressing Ctrl-F3 (while holding down the Ctrl key, pressing the F3 key)

prompts for the deletion of the entire loop or branch.  If you

did not intend to delete the current loop or branch, press the escape (Esc)

key or "N" and move to the correct sequence using the F7, F8 or F9

keys.  If the sequence is to be deleted, confirm the request by

highlighting the word "Yes", then pressing RETURN or "Y" and the loop (or

branch) will be removed.

(F4)  Insert node and element

When positioned at an element or node, pressing the F4 key allows

you to insert an element/node pair just before the current position.  You

must confirm the request and select the type of element to insert along

with a node.  You will then be asked as to if you want the same

element/node pair to be inserted elsewhere in the system between the same

node and element.  You must specifically press the "Y" key to acknowledge

this prompt.

(F5)  Plot pump (& FVH) curves

When positioned at a pump or Flow vs. Head (FVH) device, pressing the F5

key plots the curve on the screen.  If the system is balanced, the operating

point position and values are displayed.  Pressing F6 when any graphic

screen is displayed, sends the plot to the graphics printer type specified

when installing HYDRONET.

(F6)  Align tablet

If you are using a graphics tablet, you can reset the coordinate system

that your graphics tablet uses by pressing F6.  This is useful when using

drawings that are larger than your graphics tablet.  To enter node positions

from parts of a drawing not within the bounds of the tablet, simply move the

desired portion of the drawing within bounds and press F6.  You then enter

and click on two diagonal points from the new part of the drawing.  All the

points within bounds of the tablet will now be available for entry.

(F7)  Go to previous sequence (loop or branch)

(F8)  Go to next sequence

Pressing F7 places the position pointer to the first node of the previous

(lower numbered) sequence.  Pressing F8 will place the position pointer at

the first node of the next (higher numbered) loop or branch.

(F9)  Go to (or create) loop/branch

Press F9 and you will be prompted for either "Loop" or "Branch".  Once you

select the type of sequence, you will be prompted for it's number.  If you

enter the number of a loop or branch that exists, the pointer will be placed

at the first node of that sequence.  If you enter a number that is not

currently used for a loop or branch, you will be prompted for the creation

of that loop or branch.

(Ctrl-F9)  Copy loop/branch

When positioned at the last (or only) node in a sequence and press Ctrl-F9,

you can copy any other loop or branch to the current sequence starting at

the last node.  The last node that the pointer was positioned on will be

overwritten.  The copy function is useful when having to input a new loop that

has already been partially input in another loop.  You can use the F3 key to

delete nodes and elements that are not needed.

(F10)  Go to element/node

Pressing F10 prompts...         Go to...

Node   Element

Press RETURN if you wish to go to a node or press "E", space bar

or right arrow and then RETURN to go to an element.  You will then be

prompted for a node or element number.  When the number is entered, the

position pointer is placed at the occurrence of that element or node.  When

the position pointer is not moved, the F10 key is pressed again and the

same element or node number is entered, the position pointer will be placed

at the next occurrence of that element or node in the system.  This way you

can locate all occurrences of a particular element or node.

(Pg-Up)  Go to prev page (screen)

(Pg-Dn)  Go to next page (screen)

These keys allow fast movement within the screens (pages) of each loop or

branch.  The current loop or branch number out of the total number of loops

or branches and the current screen number out of the total available for

the current sequence is displayed on the lower left of the DEFINE screens.

(1..9)  Enter a previously defined element/node number

When entering loop data that has been entered previously, you can simply

enter node or element numbers at the element menu instead of having to

enter the type and then number of the element.  You have less data input and

you don't have to remember if an element is a fitting or valve etc.

REPORT

The REPORT option offers reports of element and node data, loop and

branch information, summaries of flows, head losses, pressures,

material lists, text printer configurations, hydraulic grade line plots,

pump curve graphics and 2-D and 3-D system graphics.  You will be prompted

as to whether text reports are to be sent to the SCREEN, a FILE or your

PRINTER.  Reports sent to a file can later be edited using standard word

processors.  Text reports sent to your printer will be sent through the text

printer port specified in the HNINSTAL program.  Printer reports first

request you to set the TOP-OF-FORM.  For a continuous form type printer

(dot-matrix), this can be done by setting the first line of the printer

paper at the printhead and turning the printer off and then on again.

PCX OUTPUT OF GRAPHICS SCREENS

PCX files are graphics files in a format created by Z-SOFT (Phone:

(404)428-0008).  Their PC Paintbrush program and other paint programs

can edit these .PCX graphics files.  You can add additional text,

change colors and basically perform any alteration desired.  In addition,

these programs support many more printers than HYDRONET does.  HYDRONET

supports PCX file output of graphics screen when using standard EGA,

VGA, Hercules and HYDRONET supported SuperVGA displays.  You will be ask

for a filename to send the screen to.  A .PCX extension will be added to

the 8 character filename automatically.

SUMMARY REPORT

The first screen of the REPORT - SUMMARY option lists the pipe head loss

equation used along with the flow tolerance and fluid properties on the top

of the first screen.  The bottom of the screen displays a summary of node,

element, loop and branch totals.  The following screens list pipe, fitting,

valve, pump and node data by group and are sorted by element or node number.

The basic data that was input in the DEFINE option is listed if the

current system is not balanced.  The letter "B" is placed behind the pipe,

fitting or valve numbers if the element is in a branch line.  The node

demands and heads that had a "?" entered in their fields will display

"tbs" meaning "to be solved".  If the system is balanced, then the element

data will display the flows, velocities and head losses.  Node data that

was "tbs" will now be highlighted to differentiate results from initially

fixed data.  For printed reports, "fixed head" nodes will be identified

with "fh" on the same report line.  If the flow for a directional device

(pump, check valve, PRV, PSV or FCV) is zero because of attempted back-flow,

the "Head Loss" column will display the head difference across the element

that is preventing flow.

DETAIL

The REPORT - DETAIL option provides integrated element data listed by

element and node number.  The "ALL" sub-option displays all pipe, valve,

fitting and pump data together with their optional descriptions if

desired.  The node data portion of this report is the same as in the end of

the REPORT - SUMMARY option.  If the current system is balanced, the

velocities, flows and head losses will be displayed.  You may also

obtain reports for fittings and valves, pipes, nodes, pumps and optional

descriptions separately.

The REPORT - DETAIL - PUMPS option will list pump data along with suction

node numbers and their head levels if the system is balanced.  For a quick

estimate of the Net Positive Suction Head Available (NPSHA), add the

atmospheric head (approx 33 feet or 10 meters) if using gage pressures and

subtract the vapor pressure of the liquid. (See Cameron Pages 1-10 to 1-17.)

CRITICAL

The REPORT - CRITICAL option provides a list of the 5 highest and 5

lowest pressure nodes in the current balanced system.

LOOPS

The REPORT - LOOPS option lists all loops and branches in the current system

using a  node - element - node - element - node - element - node  format.

MATERIAL

This report provides a list of the total numbers of fittings and valves

of like type and the total lengths of pipe of same diameters.

CONFIG

You may want to customize your text printer to provide more than standard

output.  Setting these parameters is optional.  You can set the

number of lines per printed text report page (the default is 60).  HYDRONET

will send TOP-OF-FORM codes when the number of lines is reached.  This

provides a skip over perforations for continuous forms or a bottom margin

for sheets.

You may also specify whether the optional element and node descriptions

are to be printed along with the standard data in the SUMMARY and DETAIL

reports.  A report of all descriptions that have been entered is available

by the  REPORT - DETAIL - DESCRIPTIONS  option.

A command string can be entered to setup your printer for any text

mode report with the INITIALIZE option.  For instance, if you want to use

the smaller internal line printer font at 8 lines per inch for the HP

Laserjet, you can enter Esc ( s 16.66 H Esc & l 8 D  and then press return

to terminate input (Esc will be displayed as "   ").  Check your printer's

user manual for control codes that may suit your needs.

You also have the option of sending your printer a command string to leave

it in a specific state at the end of reports with the RESET option.  The

standard reset command is Esc E  displayed as "    E ".

If you wish to use these parameters to set-up your text printer and

reports every time you start HYDRONET, select SAVE and the parameters

will be placed in the same default parameter start-up file as the values

set in SETUP.

GRAPHICS

Under the GRAPHICS option, you can display 2 and 3 dimensional,

hydraulic grade line and pump curve graphics.  These sub-options are

described in the following sections.

-  HGL

The REPORT - HGL option provides graphics of hydraulic grade and

elevation lines for each sequence.  Use the UP-ARROW or DOWN-ARROW keys

to display the available loops or branches or just enter the desired

sequence number.  The Y-axis is the head and elevation in feet (or

meters).  The X-axis is the distance along the loop or branch.  Thus

non-length elements such as fittings, valves and pumps are displayed as a

vertical line that represents their head losses or gains.  Major pipe

and node numbers are displayed just above the X-axis.  Potential

problems occur if the HGL drops below the elevation line (negative gage

pressures) or is far above the elevation line (high pressures).  Pressing

F6 when the HGL plot is displayed, sends the graphics plot to the graphics

printer type specified when HNINSTAL was run.

-  PUMPS

You can enter a pump or flow vs. head device (FVH) number and obtain a

display of it's curve using this option.  These are the same graphs that

are displayed in the DEFINE option using the F5 key when positioned at a

pump (or FVH).  Use the UP-ARROW and DOWN-ARROW keys to display available

pump (or FVH) numbers.

-  2-D PLAN VIEW

If you have provided x-y coordinates for the nodes in a system, you can

view it's overhead 2-D system plot.  When you first enter this option,

HYDRONET plots the system in it's entirety.  All node numbers, element

numbers and the grid system are displayed.

The various options for 2-D views are described below...

F2 - Element #s

Element (pipe, pump, fitting and valve) numbers are toggled on and off with

this option.  For very large systems, the amount of information on screen

can be very confusing and removing element numbers from view can help.

F3 - Node #'s & flows

Node number displays are toggled on and off with this option.

F4 - Loop #'s

Loop numbers are toggled on and off with this option.  Only closed regular

loop numbers are plotted and the number will be plotted in the center of

the loop.

F5 - Grids

The X-Y grid system is toggled off and on with this option.

F6 - Print

The displayed screen will be sent to the graphics printer port you specified

when you ran the HNINSTAL program.  The graphics dump to your printer takes

some time.  To interrupt the graphics screen dump, press the escape (Esc) key.

F7 - PCX output

The displayed screen will be output to a .PCX file with this option.  This

feature is only available for standard EGA, VGA, Hercules and supported

SuperVGA displays.  You must enter a name for the file and it will

automatically be appended with the .PCX extension.  You can then use any

PCX capable paint program to view, modify and print the graphics screen.

F8 - Zoom

Use this option to take a closer look at a smaller piece of a system.  You

are asked to position the top left corner of the ZOOM box (using arrow keys

on keyboard) and then press RETURN to anchor it.  You then move the lower

right corner of the ZOOM box and anchor it by pressing RETURN.  If you wish

to move the top left corner again, press the escape (Esc) key.  Once both

corners are anchored, the part of the system you have selected is

displayed.  You can use ZOOM on this new section to look at an even smaller

part of the system.  To display the system in full again, use the reset (F9)

key.  To view this smaller section in 3 dimensions, use the "Go To 3-D"

(Ctrl-F8) key.

Ctrl-F8 - Go To 3-D

Use this key to view what is currently displayed in a 3-D

format.  The options for 3-D usage are detailed in the 3-D section that

follows.  When you exit 3-D viewing by pressing the Esc (escape) key,

you return to the 2-D option.

F9 - Reset

If you have used ZOOM to view a smaller portion of the current system, you

can reset the view to the original full system display with this option.

F10 - 1:1 ASPECT

When HYDRONET displays a system or portion of a system, it plots the

view using the fully available dimensions.  A problem then occurs where,

for example, 1 inch (or 1 cm.) of the x-axis does not equal the same

distance as 1 inch (or 1 cm.) of the y-axis.  Pressing F10 brings the

display into a 1 to 1 aspect ratio without removing any of the desired

plot.  Pressing the F9 (reset) key displays the plot within the full

dimensions of your monitor again.

Esc - Exit

To return to the REPORT main menu press the escape (Esc) key.

-  3-D VIEW

Viewing a system in 3-D gives the hydraulic system designer a better

understanding of system operation, elevations and pressures.  You can

immediately observe regions of high or low pressures and other possible

problems.  You can obtain a straight-on view of the entire system for a

hydraulic grade line graphic representation.

When entering this option directly from the REPORT option, the

current system is displayed in it's entirety.  All nodes and elements are

displayed.  Use the 2-D option to ZOOM in on a specific section and then

use the Ctrl-F8 (Go to 3-D) option to view the section in 3-D.

The F2, F3, F6, F7 and Esc keys operate the same as with the 2-D option

described previously.  The following keystrokes have different functions...

F4 - Plot Hydraulic Grade Lines

If the current system is balanced, this option toggles the hydraulic

grade line graphics off and on.

F5 - Pressure heads

If the current system is balanced, this option toggles on and off the

pressure head lines (vertical lines between elevation and HGLs).

ARROW KEYS

You can change the aspect (angle) from which you view the 3-D system by

pressing the up, down, right and left arrow keys.  To make large viewing

angle changes, enter a number from the keyboard, then press the arrow key

to move that number of pixels in a particular direction (ie. to move up

50 dots of resolution, enter "50" then press the up arrow key).

PLUS (+) and MINUS (-) KEYS

The plus and minus keys expand and shrink the z axis (elevation, pressure

head and HGL scales).  This option provides a less cluttered view.

UTILITIES

DIAMETER

The DIAMETER option allows the alteration of ALL pipe, fitting and valve

inside diameters to a specified value.  If the fitting and valves were

chosen from the HYDRONET menus (not custom coefficients) then the appropriate

friction coefficients will be determined using the new inside diameter.

TITLE

You can enter a description of the current system.  This title is displayed

on the upper right of the working text screen and is saved in the system's

datafile.

NODES

The FRICTION option allows you to multiply all non-zero node demands by a

specified factor.  This allows you to investigate different operational

strategies such as what happens when peak demands double.

FRICTION

This option allows the alteration of ALL of the current system's

Hazen-William pipe roughness coefficients or Darcy-Wiesbach specific

roughnesses.

ERASE

The ERASE option clears HYDRONET memory of the current system's

data.  Datafiles on disk are untouched.  This option allows you to completely

start a new design without exiting HYDRONET.  Be sure to save any desired

changes to disk (using FILE - SAVE) before using the ERASE option.  Any

default values established in SETUP and REPORT - CONFIG will be reset.

FIXED HEAD

The FIXED HEAD option allows the setting of one "fixed flow" node's

pressure head for recirculating (no external inflows/outflows) systems.  There

cannot be any "fixed head" nodes used in the layout of a "closed loop system"

(recirculating) and the demands at all "fixed flow" nodes should be zero.  To

remove the single fixed head node, and it's pressure head, set the node number

to zero.

ANALYZE

The ANALYZE option provides a way to find potential problems in a

hydraulic design and also provides the steady-state solution to a

design using the BALANCE sub-option.

The ANALYZE sub-option analyzes the current system for data

inconsistencies.  If HYDRONET is unable to plot a graph, balance a system

or outputs strange results, ANALYZE will attempt to find the problem.  The

warnings that this option provides are strictly informational.  ANALYZE

should be run prior to balancing a system so that processing time is not

wasted.  Both a balanced and unbalanced system can be analyzed.  Use ANALYZE

after balancing a system that appears to have had a problem to obtain more

information.

The BALANCE sub-option solves the system for steady-state flows and

pressures.  The system data is first initialized, then briefly interrogated

for completeness, initial system flows are estimated and the iterative

process of adjusting system flows begins.  Press escape to interrupt the

process if the total adjustments to flows does not tend to converge toward

zero or if the set flow tolerance might be too small to allow a solution

within a reasonable amount of time.

If the iterations are taking a long time and you do not want to wait for

the tolerance to be reached, you can press F2 to end the iterations and

solve for final head values.  There may be some large errors in the final

head check though, because the flow adjustments weren't performed all

the way to the set tolerance.  NOTE: Be sure to note any error or warning

messages that are displayed on the screen after the system is balanced.

There may be some important warnings about your results.

Various statistics are displayed in the balance box.  The first line

shows the iteration number and control valve iteration number.  Because

some control valves induce head losses (ie., PRVs), the whole system

must be balanced and then head losses adjusted for proper valve operation

and the system balanced again.  The control valve iteration number

displays how many times valves were adjusted.

The second line displays the total of flow adjustments for each iteration.

This is the total flow adjustment to all elements.  This number should get

smaller on each iteration.

The third line displays the percent of convergence.  This number is the

percentage of the time the flow adjustments converge (get smaller).  This

number gets close to 100% for a solidly converging system.  If the percent

convergence is in the 80 to 100% range but flow adjustments still reach the

set flow tolerance, everything is probably fine.

The fourth line shows the maximum head error detected when the system heads

were calculated.  This number is obtained by calculating each element's

head loss (using the flow that was determined for it during the balancing

routine) and comparing that to the head value at the downstream node.  This

number should be very small for a properly balanced system.  The value of

maximum head error will flash if the error is greater than 1% of the largest

element's head loss.  If more accuracy is desired and the system seems to

converge well, you can lower the flow tolerance in the SETUP option.  It is

up to you, the engineer, to decide what is an acceptable head error.  If you

have pipes in a system with 100 foot head losses, a maximum head error of

.5 foot may be acceptable.  However, if you have a maximum pipe head loss

of 3.0 feet, an error of only .01 foot may be acceptable.

At the end of the fourth line of the balance box, is the total elapsed time

for the balance.  This is available so that differing system configurations

can be compared for speed of convergence.

If AUTO PIPE LENGTHS data field is set to " YES " in SETUP, then when

ANALYZE or BALANCE is selected, all pipe lengths will be recalculated if

node coordinates are being used.

QUIT

This option is used to exit HYDRONET and return to DOS.  Be sure to save

any desired changes since the last file update using the FILE - SAVE

option.  Pressing "N" or the escape (Esc) key returns you to HYDRONET's main

menu.  You must press "Y" to leave HYDRONET.

USING THE EQUIVALENT LENGTH METHOD

When modeling fluid transport systems that convey fluids other than

water, you can have HYDRONET use the equivalent length method for fitting

and valve head losses.  This method essentially models fitting and valve

friction in terms of the equivalent friction of turbulent flow through

lengths of standard steel schedule 40 pipe having a specific roughness

of .00015 feet (.0457 mm).

To use this technique, enter the SETUP option and specify the

Darcy-Wiesbach equation for use.  A field will appear to specify that

HYDRONET use the equivalent length method (USE EQUIV LENGTHS?) on the

current system.  Set this parameter to "YES" by pressing the right or left

arrow keys.  Now when you specify a certain fitting or valve type and input

an inside diameter, HYDRONET will calculate a length of steel pipe that

will approximate the same resistance.  The calculation is based on the "K"

coefficient for water flow for the valve, the diameter of the valve and

the friction factor for complete turbulent flow in steel pipe for this

diameter.  The K value is multiplied by the diameter and divided by the

friction factor to obtain the equivalent length. (See Cameron page 3-119.)

All "K" values that appear in HYDRONET when the equivalent length

method is specified must be for use with water.  These "K" values

are used in the calculation of equivalent lengths.  If you have "K"

values for fittings and valves for use with fluids other than water,

do not specify the use of the equivalent length method.  Do a manual

equivalent length modeling of fittings and valves that you do not have

non-water "K" values for.  These non-water fittings and valves should be

modeled as steel pipes with the specific roughnesses listed above.  To

compute the equivalent length of pipe, see Cameron pages 3-119 to 3-122.

DESIGN METHODS

1.  Using a plot plan of your system, label all nodes with numbers

and note those with "fixed heads" (sources and discharges with known or

desired pressure heads).  Nodes are placed before, after and between

elements (pipe, fittings, valves, fittings & pumps).

2.  Label all elements with numbers.  Use a numbering scheme that will make

it easy to determine where certain elements and nodes are in the system.  For

example, all nodes and elements that start with 100 (ie, 101,102,etc.) will

be in the first main line. (See example problem 6.)  Obtain pump curve data,

pipe roughnesses, valve types and other needed information.

3.  Create loops making sure all "fixed head" nodes are connected

to at least one other "fixed head" node (w/dashed lines) forming

pseudo-loops.  Try to have loops adjacent to the next and previous numbered

loops (ie, loop 2 adjacent to loop 1 and 3).  Number all loops.  Identify

fixed outflow branch lines that are not to be a part of the loop system.

4.  Start HYDRONET and enter the SETUP option and set the head loss

equation, units, fluid parameters and flow tolerance.  If these conditions

are going to be used for most designs, you may wish to place them in the

default parameter file for automatic start-up.

5.  Use the DEFINE option to start entering system data.  If a portion of

the system can be designed to operate on it's own, starting small will give

you a better feel for HYDRONET's operation.  Start off by entering the system

data without any control valves.  Only after having solved the system without

control valves, use the valves to control pressures and/or flows.  Enter any

branches using the DEFINE - BRANCHES option.

6.  Run the ANALYZE option to identify any incomplete or inaccurate

data that might cause problems.

7.  When data has been newly entered and after running the

BALANCE routine regularly, use the  FILE - SAVE option to save your work.

8.  Run BALANCE to obtain a solution for the system.  Be sure the percent

convergence is high and that the maximum head error is acceptably low.

9.  Use the REPORT - CRITICAL option to obtain a summary of highest

and lowest pressure nodes and possible pump problems and observe the

hydraulic grade line, 2-D and 3-D graphs.  Use the REPORT - DETAIL option to

observe velocities in pipes and excessive head losses.  Go back to step 5

and using F9 and F10, edit node and element data accordingly.

DESIGN TIPS - TROUBLESHOOTING

- When a pump is restricted to a specific location and the

suction head is low, the diameters of the suction side lines can be increased

to minimize intake losses or a booster pump may be needed somewhere up-stream.

- When a pump is not restricted to a specific location, the insert element

function (F4) and the delete element function (F3) can be used to move the

pump to various positions in the line and provide an adequate NPSHA.  Use the

F9 key to locate pumps by element number.

- When inserting elements and nodes that will be present in two adjacent

loops in an existing design, use the F9 and F10 keys to locate all occurrences

of adjacent elements and nodes.

- Use more pseudo-loops in small systems that contain many pumps and check

valves if convergence is a problem.

- If two or more pumps are in the same loop (especially if adjacent) they

should also appear in other loops in the system (use pseudo-loops if possible)

for stability of convergence.

- If a design is not converging, and there are pumps in the system,

enter the DEFINE option and use the F9 key to locate all the pumps.  Press

F5 when positioned at a pump to make sure curves are always decreasing

(ie, drops toward the x-axis).

- If a design is not converging and has a fixed head loss (FHL) device,

try removing the device and then if it converges, reduce the original amount

of fixed head loss.  The loop must provide enough head (through pumps or

static heads) to overcome the fixed head loss.

- Try not to have to directional devices oppose each other in the same

loop.  For example, while tracing a loop, a check valve allows flow in the

forward direction and two elements away a pump allows flow only in the

backward direction.  This will not allow for the flow in the loop to be

adjusted easily.

EXAMPLE PROBLEMS

The datafiles for these example problems are included on the HYDRONET

diskettes and were loaded into the main HYDRONET directory

created by HNINSTAL.  To review them, use the  FILE - RETRIEVE  option

to retrieve the data, then the  DEFINE  and  REPORT option to edit and

display their data.

PROBLEM  1

This simple example introduces the use of pseudo-loops with "fixed head"

nodes in a gravity flow (no pump) problem, using the Hazen-Williams equation

in English units.

The gravity flow system depicted in the following 2-D plot is to be solved

for steady-state flows and pressures.  We identify the needed loops for the

system by first finding all points of unknown inflow and outflow.  The

system contains three of these which are "fixed head" nodes 1, 11 and 15 at

reservoir inlets and exits.  All other nodes are of the "fixed flow" type

(flow is fixed at zero, head is to be determined).  This system requires at

least two pseudo-loops to include the three "fixed head" nodes and all

elements in the analysis.  Every "fixed head" node must be connected to at

least one pseudo-loop and it does not matter whether the loop goes from

node 1 to 15 and 1 to 11 or if they connect 1 to 15 and 11 to 15.  Three

pseudo-loops could have been used but that many are not required.  If

convergence problems were to occur, a third pseudo-loop could be tried for

added stability.  There are no elements left out of these two loops so there

is no need for any internal closed loops.  The elements (pipes, fittings and

valves) are numbered sequentially starting at 1 and ending at 14.  Nodes are

also numbered sequentially starting at 1 and ending at 15.

This system contains no branches.  Any one (but only one) of the three

lines could be modeled as a branch with one pseudo-loop.  The two "fixed

head" nodes would drive the flow in the system and the branch would have

simple head loss calculations made on it.  The flow in the branch would be

fixed and you would have to ensure that the head at the end of the line

would be met.

After starting up HYDRONET, enter the SETUP option and select the

Hazen-Williams equation for use in calculating pipe head losses.  Specify

English units of gpm for flow and psi for pressure for use in this

design.  Set the flow tolerance to .01 gpm.  We will be using cast-iron

pipe so we'll set the default Hazen-Williams Friction Factor C to 100.  When

inputing numbers, you can simply press the space bar once after entering

the number on the left of the field and the text to the right will be

ignored.  If we were going to be using these conditions for most all of our

designs, we could update the default parameter file with these

settings.  HYDRONET will then be automatically setup to use these values

and settings at start-up.

To enter element and node data, enter the DEFINE option and select

"LOOPS".  A prompt for a loop number appears and we'll keep things simple

and enter "1".  A prompt appears and the number of "1" is displayed as

the next available node number.  We'll start at the top of this design and

type "15" over the default and press RETURN.  If we had input a unintended

node number, we could simply press the escape (Esc) key and input the node

number again.

The node data fields appear in a window for input.  We have the option of

entering a description for the node.  The use of the optional

description for nodes and elements quickly uses up memory available for

other data items.  Next, we enter the elevation of the reservoir and

press RETURN.  Since this is a "fixed head" node where the outflow or

inflow of the reservoir is to be determined we enter "?" (question mark)

for the demand and press RETURN.  This tells HYDRONET to solve for the

flow.  There is no pressure component at this node (open surface reservoir)

so we enter zero for the head and press RETURN again.  We also have the option

of entering X-Y coordinates for the node.  These coordinates are not needed to

obtain a balanced solution.  They make automatic pipe length calculations and

the viewing the system in 2-D and 3-D available.

The element menu appears and we press the down arrow key once so "Fitt"

is highlighted and press RETURN.  We are prompted for an element number

and type "14" over the default value and press RETURN.  The fitting

menu appears and we use the arrow keys to highlight "Inlet" and press

RETURN.  A sub menu appears and again we use the arrow keys to highlight

"flush - sharp-edged" and press RETURN.  Again, a field for optional

description appears and we press RETURN to skip over it.  We enter "4.03" for

the inside diameter of our 4 inch pipe.  This establishes the default

diameter for the system and from now on "4.03" will appear in all

diameter fields until a different diameter is entered.

The node number field appears again and we enter "14" and press RETURN.

We skip the description field and the elevation field has the value that was

used on the other side of the fitting.  This is not correct in this instance

because that value is the elevation of the water surface, so we enter the

actual elevation of the discharge side of the fitting.  This is a "fixed

flow" node where we want the head to be determined.  There is no demand flow

out of this node so we enter 0.0 or press space bar repeatedly and press

RETURN.  The head at this node is "to be solved"  so we enter "?" in the

head field and press RETURN.

The element menu then appears and we press the arrow down key until

"Valve" is highlighted and press RETURN.  The prompt for element number

appears and we type "13" over the default value presented.  "Gate Valve" is

highlighted and we simply press RETURN to specify that type.  The valve

data fields appear and we press RETURN twice to skip the description and

accept the default diameter.

At the node number field we enter "13", enter it's ground elevation and,

since there is no demand flow, enter 0.0 then a "?" in it's head field.

The element menu reappears and we press the arrow down key until "Pipe" is

highlighted and press RETURN.  Enter "12" over the default pipe number.  We

press RETURN twice to skip the description and accept the default

diameter.  The length will be left at zero since we are inputing node

coordinates and want HYDRONET to determine the length of pipe.

We continue to enter element and node data in sequence.  Element #5 and #6

are the friction components of a Tee fitting.  Both represent the

branch component of a Tee fittings friction loss.  The current pseudo-loop

data input ends with node 1 where the elevation is entered, a "?"

for demand and zero is entered for it's pressure head.

Press F9 to start the input of the next pseudo-loop #2.  Since this

loop has some common elements and nodes with loop #1, we can enter a single

node for loop #2 of any number and press RETURN to accept all defaults.  We

reposition the pointer back to that node and press "Copy Loop" (Ctrl-F9)

key.  We can now specify loop #1 and HYDRONET will copy it to this

loop.  The single node that we entered will be overwritten.  We can now

delete element and node pairs that are not common between the two loops.  The

remaining needed elements and nodes can now be inserted by using the F4

(insert) function at the beginning of the loop.

Occasionally and especially when all your data is entered,  you should save

your work by entering the FILE option, selecting the SAVE sub-option, specify

a filename and then press RETURN.  The ANALYZE option should be used to

examine the data for completeness and if no errors are found, the system

can be solved by using the BALANCE sub-option under the ANALYZE main option.

The REPORT - SUMMARY report displays the flows through each pipe, fitting and

valve along with the direction, velocity and head loss.  Node data displays

the demand (if negative out of the system, if positive into the system).

Pressures and hydraulic grade lines in feet are displayed with the

fixed heads identified.  The REPORT - DETAIL option report

lists all elements by type and presents the same data fields as the SUMMARY

report.

PROBLEM  2

This example problem demonstrates the use of the Darcy-Wiesbach equation to

calculate pipe head losses, the use of branch lines, a supply from a "fixed

head" force main and discharge to the atmosphere.

Node 1 is a force main supplying 60 degree F. water at a pressure of 100

psi.  A requirement of at least 1000 gpm at 40 psi is needed at node 14.  The

branch line is to deliver 300 gpm to node 16 and 200 gpm to node 19.  Two

booster pumps are to be used to deliver this flow.  At least one pseudo-loop

is required for this open (external sources and discharges) system. We can

then model the other line as a branch of fixed flow.

Using the SETUP option, we specify the Darcy-Wiesbach equation for

calculating pipe head losses.  We then setup the desired units system and

units of flow and pressure.  The value of .00015 feet is entered for the

default specific roughness.  The kinematic viscosity is set to .00001216

ft2/sec.  Since the fluid is water at 60 degrees F, we can use the standard

fitting and valve coefficients that are automatically input from the

menus.  If this were a fluid with a different viscosity, we would use the

equivalent length method for the modeling of fitting and valve losses.

The force main at node 1 provides water at an elevation of 210.55 feet

and a pressure of 100 psi.  A "?" is entered in the demand field and the

pressure is entered for the node's head.  At node 14, an elevation of 561.83

is entered, a "?" is entered in the demand field and a pressure of 40 psi

is entered for the head.  All other nodes in the system will have

a "?" entered in the head field and of those, only nodes 16 and 19 will

have non-zero flow demands.  The system's pipe, fitting and valve diameters

will be adjusted along with booster pump curves to provide the desired

flows and pressures.

The design arrived at in the following pages is just one possible solution

to this problem.  Trade offs of pipe and pump sizes and operating energy costs

exist and in general a least cost approach would be used.  Pumps should be

placed so that possible cavitation situations are avoided.  The 3-D graph of

the system shows that all line gage pressures are positive.

PROBLEM  3

This problem demonstrates connecting two small sub-networks with a single

line, using the Hazen-Williams equation and branch lines.  The minor friction

losses from fittings and valves will be neglected in this preliminary design.

A single reservoir supplies water to two small networks.  The first network

(outlined by pipes #2, 3, 4, 13, 12, 11, 10 and 9) is on a plateau of

approximate elevation 240'.  Pump 16 provides additional pressure to the

second pressure zone (pipes #18, 19, 20 and 21) on a plateau of approximately

350'.  The design objective will be to provide flow at all

points of demand of .5 cfs at a head above 40 psi.  A pseudo-loop is used so

that each network is not considered isolated.  Nodes #17 and #1 will have

undetermined flows and the system will have to be adjusted (pipe diameters

and pump curve) so that the flow at node 1 will be close to .5 cfs.  The two

networks are connected by a single pipe and pump line.

The information for the "fixed head" node at the supply reservoir

(node #17) will be a water surface elevation of 524.33', a "?" for demand

and zero for the pressure head.  The information for node 1 will be the

ground elevation, a "?" for demand and a value of 50 psi for head.  The

demands at the various other nodes will be entered as negative values (out

of nodes) so that the node reports will display flow into (+) and out (-)

of nodes properly.

Minor losses from fittings and valves can be inserted into the system at a

later time once all the system is adjusted to provide close to the pressures

and flows needed.

APPENDIX  A

ERROR MESSAGES

TABLET USE

" Possible tablet or port problem! "

Problem:    HYDRONET tried to poll the graphics tablet through the port

specified when you ran HNINSTAL but did not receive a response.

Remedy:     Be sure the port is setup with DOS's MODE command (See Operation

section earlier).  Also enter the SETUP option and verify that

the graphics tablet is setup as desired.

" Points must be diagonal! "

Problem:    HYDRONET must perform a mathematical translation from the tablet

coordinates to your drawing coordinates.

Remedy:     The two alignment points from your drawing must be on opposite

corners of the pad (ie, x1 cannot equal x2, and y1 cannot equal

y2).  Use the F6 key while in DEFINE to realign your drawing.

PUMP OPERATION

" Pump # flow is larger than last point of curve! "

" Pump # flow = # (off of curve)! "

Problem:    During the balancing routine, the pump in question has a flow

that is more than 3 times the flow increment for the pump.

Remedy:     This can signify a potential problem if the system is not

converging.  If the message disappears when the system is finally

balanced most likely no problem exists.  If it doesn't, make sure

your pump curves decrease in head for increasing flow (drop

toward the flow axis).  Use the F10 key in the DEFINE option to

find the pump and press F5 to plot.  Final pump flow should be

between the 2nd and 4th point on the curve.

" Warning: Valve # direction opposes a pump or valve in same loop! "

" Warning: Pump # direction opposes a pump or valve in same loop! "

Problem:    HYDRONET detects two directional devices (pumps and/or valves)

whose specified flow directions oppose each other.

Remedy:     This is just a warning.  Having two directional devices in the

same loop that allow flow only in opposite directions penalizes

the balancing routine.  If the system fails to converge, enter

the DEFINE - LOOPS option and use the F9 key to locate the pump

and/or valves in question.  Attempt to place these directional

devices in separate loops.

" Cannot plot pump curve! "

" Cannot obtain curve for pump #! "

" Error fitting pump curve! "

Problem:    The data for the pump cannot be fit to a cubic equation so that

HYDRONET can have a continuous function of head vs. flow to work

with.

Remedy:     Enter the DEFINE - LOOPS option and use the F9 key to find the

specified pump.  Edit the data so that if F5 is pressed when

positioned at the pump, it can be plotted.  Pump curves can be

plotted from the REPORT - GRAPHICS - PUMPS option.

" No flows, be sure total pump shutoff head is at least #"

" No flows... no head difference driving system! "

" No flows, check pumps, valves or lower tolerance...  "

Problem:    This error can occur because...

- the flow direction of pumps and/or directional valves oppose

each other.

- weak pumps in a system are not able to overcome the static head.

- there is no static head driving the flow in a non-pump system.

Remedy:     Check pump and valve directions.  Check pump shutoff heads to be

sure they are large enough to push flow against the static head

opposing them and be sure that a static head is present in

non-pump systems.

" Pump # curve is not always decreasing. "

" 2nd pt should be less than shutoff! "

Problem:    Pump curves should always decrease. The shutoff head should be the

highest head value, the next point on the curve should be the next

highest and so on.

" Pump # flow is less than 2nd pt on curve, straight line approx used."

Problem:    The flow determined for the pump was less than the flow increment

for the curve.

Remedy:     If the flow is lower than the 2nd point on a pump's curve, the

head addition is calculated using a straight line approximation

between the shutoff head and the 2nd point.  For HYDRONET

to properly model pumps, the optimal operating point for the

curve should be placed around the 3rd point of the curve.

FILE INPUT/OUTPUT ERRORS

" Error opening file HN.CNF!  Rerun HNINSTAL... "

" Cannot find HN.CNF!   Run HNINSTAL or enter

directory path where HYDRONET system files are (Q=quit): "

Problem:    HYDRONET can not find the file that contains information on your

hardware configuration (HN.CNF).

Remedy:     If you are running HYDRONET from another directory, be sure the

HYDRONET directory is listed in your path (see your DOS manual).

If you reside in your HYDRONET system directory, run HNINSTAL,

and make sure the HN.CNF file is present in the directory.

" HN.HLP not found! (gone or bad path) "

Problem:    HYDRONET can not find the file that contains help information that

is available when F1 is pressed.

Remedy:     There should be a file named HN.HLP in the HYDRONET hard disk

directory.  Re-run HNINSTAL if there is not!

" Error - not a HYDRONET data file! "

Problem:    You have attempted to retrieve a file that is not a HYDROFLO

(*.FLO) or HYDRONET (*.NET) datafile.  The file requested

must have been created by HYDRONET.

" Not HYDROFLO 1.2 or 1.1 data file! "

Problem:    You have attempted to retrieve a file that is not a

HYDROFLO datafile with a " .FLO " extension.  The

file requested must have been created by HYDROFLO.

" Coefficient file not found! "

" File  HN.VAL  not found..."

Problem:    HYDRONET cannot find the files (HN.VAL and HN.FIT) that contains

the preset fitting or valve coefficient data for water systems.

Remedy:     Be sure that all files on the distribution diskette (other than

".NET" datafiles) are in the same directory as the HN.EXE file.

You can execute HYDRONET from any directory but all system files

must be together.  Re-run HNINSTAL if using a hard disk system.

" No files in data directory! "

Problem:    If you have gotten this message and you know there are data files

out there somewhere, the default data directory is not specified

properly or there are no datafiles in your directory.

Remedy:     Enter the SETUP option in HYDRONET and specify the correct default

data file directory.  If you will be using this same directory

often, consider updating the default parameter file so that this

directory is always looked at upon start-up.

BALANCING ERRORS

" Cannot set initial flows. Node # demand cannot be routed to fixed head! "

Problem:    This error message occurs because part of the network is isolated

(ie, check valve or pump flow directions do not allow flow into

a portion of the network).

Remedy:     Locate the stated node (use F10 in define) and attempt to trace

it's flow through the system to a "fixed head" node.  Note pump

and control valve directions to see if the flow is blocked.

" System not converging! Check data! "

Problem:    Some instability is present not allowing the system to converge.

Remedy:     Run ANALYZE.  Check pump curves to see if a pump is too small

or the pump curves are not decreasing.  Try adding extra

pseudo-loops to the system if possible.

" Loop # must start/end w/ fixed heads (psloop) or w/ same node (closed)! "

Problem:    A pseudo-loop in the system does not begin and end with "fixed

head" nodes or a closed loop does not begin and end with the

same node.

Remedy:     Enter the DEFINE - LOOPS option and use the F7 and F8 keys to move

to the loop in question.  Check beginning and ending nodes to be

sure they are "fixed head" nodes if using pseudo-loops.  Be sure

that closed loops begin and end with the same node.

" ERROR:  Flows from fixed head nodes don't total zero! "

" Sum of flows at node # not equal zero! Check results! "

" In and out demands at nodes do not total zero! "

Remedy:     These errors should not occur in straight forward piping designs.

These are HYDRONET internal errors.  If you get one of these

errors, prepare to send us a disk with the datafile on it.

GENERAL ERRORS

" Out of memory for this file! " or

" Out of memory for description! " or

" Out of memory for this file! " or

" Out of memory for pipes, valves, pump or node! "

Problem:    Available RAM memory is used up.

Remedy:     Uninstall any memory resident programs, add memory chips to

bring total memory up to 640K or clear any unnecessary

description fields.  HYDRONET limits are 3000 elements

and 3000 nodes.

" Must get node data! "

Problem:    HYDRONET requires that a node be placed here.

Remedy:     If the node is not needed and to be deleted later, simply

press RETURN repeatedly to get past this node.

" Must have at least one loop! "

Problem:    You cannot delete a loop if it is the only loop in the system.

Remedy:     If you want to clear HYDRONET memory of all current data,

use the UTILITIES - ERASE option.

" Number used for different element! "

Problem:    You have specified an element number that has been used before

for another type of element.  HYDRONET makes sure that numbers

are not duplicated in differing types of elements.  You must

use different element numbers for each element.

" Must enter a loop first! "

Problem:    You have tried to enter data for branch pipe section when the

system does not have a loop that the branch can flow from.  Enter

a loop first.

" Warning, Loop # doesn't have an element in another loop! "

Problem:    HYDRONET has found an isolated loop that does not have any

elements in common with any other loop.  This may lead to

unwieldy results.

Remedy:     A pseudo-loop should be created if a closed loop cannot be added

to link the isolated loop to the rest of the network.

" Element # has different start and end nodes! "

Problem:    While HYDRONET was initializing the system data, it found that a

certain element had different specified starting and ending nodes.

Remedy:     Enter the DEFINE - LOOPS option and use F9 to locate the

specified element.  Press F9 and specify the element number again

to locate all the occurrences of the element and find where the

mistake lies.  An element can only have one unique beginning

and ending node.

" Cannot have fixed head after PRV #! "

" Cannot have fixed head before PSV #! "

Remedy:     You cannot have a fixed head node just downstream from a pressure

reducing valve (PRV).  HYDRONET knows to supply enough head loss

to drive the pressure down to the specified level.  HYDRONET also

notes the pressure upstream of a pressure sustaining valve (PSV)

to try and maintain the desired pressure level.

" No X - Y coordinates defined for system! "

Remedy:     You cannot look at 2-D or 3-D graphics if you haven't input X,Y

coordinates for nodes.

" Unable to estimate initial flows! "

Problem:    HYDRONET was unable to set up a initial flow grid for the system.

Remedy:     Most likely check valves and/or pumps are isolating a portion of

the network and HYDRONET cannot trace a set demand to a supply or

outflow "fixed head" node.  Use the REPORT - SUMMARY option to

check demands at nodes and locate all check valves and pumps to

be sure their flow directions are correct.

" System must be balanced! "

Problem:    You cannot observe data on the REPORT - CRITICAL option or look

at Hydraulic Grade Line plots if the system is not balanced.

" Must use a defined valve or fitting! "

" Must use a previously defined pump! "

" Must use a previously defined pipe! "

" Must use a previously defined node! "

Problem:    You have run out of memory or reached the limits for the number

of the type of elements or nodes.

Remedy:     HYDRONET has a limitation of 3000 elements (consisting of 3000

pipes, 1000 fittings and valves and 300 pumps.  If you

have run out of memory, you can add more memory to reach

640K or remove some memory resident programs from main

memory or you can combine some pipes into longer sections

or delete unnecessary optional descriptions.

" Must enter defined element number! "

Problem:    If inputing element numbers when the element menu is displayed,

you can only input previously defined elements.  Press escape

to get back to the element menu and select the type of a new

element.  Then input it's number if not previously defined.

" Can't have both unknown flow and head! "

" Cannot set both demand and head! "

Problem:    You can only set one parameter, either the pressure head or the

demand flow at a node.  HYDRONET will solve for the unknown

parameter.

" Cannot have fixed heads in branches! "

Problem:    You cannot have "fixed head" nodes in a branch.  Simple head

loss calculations are performed in branches as the flow is

fixed.  If you wish to set the head and have the flow

determined, convert the branch to a pseudo-loop.

" Demand must be out of node (negative)! "

Problem:    All fixed demands at nodes are outflows and are represented by

negative values.  If you want to fix the head level and determine

the possible inflow, make that node the beginning or end of a

pseudo-loop.

" Error in sequence! "

Problem:    When deleting a node/element pair, you are prompted whether you

want the pair deleted everywhere else in the system where they

exist.  This message occurs when HYDRONET finds the node/element

pair elsewhere but the sequence (the adjacent nodes and elements)

are not consistent.  HYDRONET will not delete the pair where

that occurs.  Use F10 to locate the remaining occurrences of the

pair.

" Warning, Branch #, starting node #d isn't in main network! "

Problem:    The starting node in a branch must exist in the main network.

This is how HYDRONET knows the total head for the simple head

loss calculations performed on branches.

" Error!  Node # doesn't start or end a pseudo-loop! "

Problem:    All "fixed head" nodes must start or end at least one

pseudo-loop.

" No fixed head in system, use UTILITIES-FIXED HEAD to set head...  "

Problem:    HYDRONET has balanced the system but has found no fixed head

to use as a starting point for head.  No HGL's or nodal pressures

can be calculated.

Remedy:     This is not a problem unless you want hydraulic grade lines

computed.  Use the UTILITIES-FIXED HEAD option to set one

node's head and allow nodal pressures to be computed for

recirculating (no external inflows or outflows) systems.  There

should be no pressure heads set when inputing node data for

recirculating systems.

" Pipe # length is zero and one or more coordinates are zero! "

Problem:    If you are inputing coordinates for nodes, do not set any at

zero.  Use zero to have HYDRONET ignore the coordinate and not

plot it.  If you've left pipe lengths at zero so that they will

be calculated, you cannot leave adjacent node's coordinates at

zero.

" Pipes are not on both sides of enlargement/contraction # ! "

Problem:    Pipes are needed on both sides of an enlargement/contraction

(reducer) to determine the head loss for the fitting.  Put

pipes on both sides of this type fitting even though they may

be short.

" No pipe on either side of nozzle/orifice # ! "

Problem:    At least a short section of pipe is needed on one side of the

nozzle/orifice to calculate the head loss.

APPENDIX  B

Metric D-W Specific Roughnesses

Darcy-Wiesbach specific roughnesses in mm.

(Source - Pipeflow analysis by Stephenson, 1984)

Finish                              Smooth     Average     Rough

______________________________________________________________

Glass, drawn metals                   0          0.003      0.006

Steel, PVC or AC                      0.015      0.03       0.06

Coated steel                          0.03       0.06       0.15

Galvanized, vitrified clay            0.06       0.15       0.3

Cast iron or cement lined             0.15       0.3        0.6

Spun concrete or wood stave           0.3        0.6        1.5

Riveted steel                         1.5        3          6

Foul sewers, tuberculated

water mains                    6         15         30

Unlined rock, earth                  60        150        300

APPENDIX   C

COMMON UNIT CONVERSIONS

MULTIPLY                           BY                      TO GET

________________________________________________

centistokes                      1x10-6              square meters / sec.

cubic ft/sec (cfs)               448.8               gpm (US)

cubic ft/sec (cfs)               .028317             cubic meters/sec.

cubic meters/sec                 1000.               liters per second

feet (length)                    .30480              meters

feet of liquid                   SG/2.31             psi

gpm (US)                         .06309              liters per second

gpm (Imperial)                   1.20094             gpm (US)

inches                           25.4                mm. (millimeters)

liters/sec.                      15.85               gpm (US)

Kpascals                         .1450               psi

Kpascals                         .102/SG             meters of liquid

meters (length)                  3.2808              feet

meters of liquid                 SG/.102             Kpascals

Million gal/day (MGD)            .0438               cubic mtr/sec

Million gal/day (MGD)            694                 gpm (US)

mm (millimeters)                 .0394               inches

pounds/sq.inch (psi)             6.8948               Kpa

pounds/sq.inch (psi)             2.31/SG              feet of liquid

SG is specific gravity (See Cameron pages 4-37 to 4-45)

(for kinematic viscosity conversions, see 4-25 in Cameron)

APPENDIX  D

ATMOSPHERIC PRESSURES AT VARIOUS ALTITUDES

ALTITUDE                          PRESSURE

FEET            METERS              Psia           Kpa

-1000            -304.8              15.2          104.8

-500            -152.4              15.0          103.4

0                 0              14.7          101.4

500             152.4              14.4           99.3

1000             304.8              14.2           97.9

1500             457.2              13.9           95.8

2000             609.6              13.7           94.5

2500             762.0              13.4           92.4

3000             914.4              13.2           91.0

3500            1066.8              12.9           88.9

4000            1219.2              12.7           87.6

4500            1371.6              12.4           85.5

5000            1524.0              12.2           84.1

5500            1676.4              12.0           82.7

6000            1828.8              11.8           81.4

6500            1981.2              11.5           79.3

7000            2133.6              11.3           77.9

7500            2286.0              11.1           76.5

8000            2438.4              10.9           75.2

8500            2590.8              10.7           73.8

9000            2743.2              10.5           72.4

9500            2895.6              10.3           71.0

10000            3048.0              10.1           69.6

15000            4572.0               8.3           57.2

20000            6096.0               6.7           46.2

30000            9144.0               4.4           30.3

40000           12192.0               2.7           18.6

50000           15240.0               1.7           11.7